- Incident Chronology at Peach Bottom Atomic Power Plant: 1974- 2012

Philadelphia Electric's (PECO) applied for a license to operate the

Peach Bottom Atomic Power Station in late-July, 1960. The application

was approved by the Atomic Energy Commission. Peach Bottom was a 40

megawatt, High Temperature Graphite Moderated reactor that operated

from 1966-1974.

Peach Bottom 2 & 3 , are 1,065 megawatt Boiling Water Reactor designed

by General Electric and engineered by Bechtel. Both reactors began

operation in July, 1974, but had their licensees extended by the Nuclear

Regulatory Commission (NRC) and are expected to operate though 2034.

The Nuclear Regulatory Commission (NRC) and the Institute for

Nuclear Power Operations (INPO) have clearly demonstrated that

Philadelphia Electric's (PECO), renamed Exelon in 2000, performance has

historically been lackadaisical and sub-par. In order to put Peach Bottom's

operating history into perspective, it is necessary to review PECO's plant

legacy.

According to Eric Epstein, Chairman, TMI-Alert: "Managerial

problems further aggravate and compound the inherent flaws with Peach

Bottom's reactor and containment structure." The reactors at Peach

Bottom are General Electric (GE) Boiling Water Reactors (BWR). Epstein

noted, "The GE-BWR is an obsolete design no longer built or constructed.

Many in the industry feel it is inferior to Pressurized Water Reactors.

Obviously the age of the reactors, and the subsequent embrittlement that

ensues, further erode the margin of safety."

Peach Bottom's Mark 1 containment structure has been

demonstrated by Sandia Laboratories to be vulnerable during a core melt

accident. Epstein explained: "The containment is likely to fail during a

core melt accident [like Three Mile Island] allowing radiation to escape

directly into the environment." Nuclear industry officials say the problem

with the Mark 1 is that it is too small and wasn't designed to withstand the

high pressure it is supposed to resist.

1974 - Peach Bottom came on line at a cost of $375 per

kilowatt.

March, 1983 - A spill of 25,000 gallons of radioactive water was

reported at the plant.

June 1983 - PECO was fined $40,000 by the NRC for a valve

violation.

July 1983 - Philadelphia Electric identified cracks in their cooling

pipes.

1983 -1987 - PE was issued a number of violation notices that cost the

utility $485,000 in civil penalties. All the violations involved failure of

personnel to follow procedures.

Examples of violations include: workers entering high radiation areas

without required radiation protection; improperly controlling access keys

to the plant's high radiation areas; discrepancies in workers' radiation

work permits; improper packing of low level radioactive wastes; leaving

air lines open while the reactor was producing power between August 12

and September 10, 1982. With these lines open the containment could not

be sealed against radiation escape in the event of an accident; allowing

excessive leakage from the containment building; improperly setting

instrument valves which made the plant incapable of providing back-up

signals to automatically shut the reactor down in the event of an accident

(Lancaster Independent Press, April, 1988).

Ronald Haynes, the NRC's regional administrator, stated, "These

violations demonstrate the need for improvements in the control

of operational activity."

June 19, 1984 - The NRC cited PECO for five alleged violations of

technical specifications at Units 2 and 3. The NRC also proposed a

$30,000 fine.

Three of the alleged violations "involved exceeding the maximum

allowable reactor heatup rate, allowing pressure in the reactor to go

beyond the limit specified for a given temperature and failing to recognize

that a control rod was inserted into the reactor at a rate slower than

required."

Continued on the next page...

The other two violations "involved changes to facility procedures in

1977-1979 that were not properly reviewed and three instances in 1980

and 1983 of failures to follow procedures." These violations were identified

by an inspector between January 5 and 20, 1984 ( United States Nuclear

Regulatory Commission, Office of Public Affairs Region I, June 19, 1984).

December 1984 - An Institute of Nuclear Power Operations (INPO)

evaluation found "clear evidence of declining performance". In

addition, the report claimed that these problems were "longstanding."

- 1985 - An NRC inspector observed a Peach Bottom operator dozing at

the controls. No safety violation was charged.

June 1985 - The plant was shut down due to mechanical problems.

July 26, 1985 - PECO was accused of pressuring the United

Way to deny eligibility to Del-AWARE Unlimited, Inc., "a group that is

lobbying against the water-diversion project that would supply the

utility's Limerick power plant...I wouldn't go as far as to use the word

threatened, but the message was clear. PE would stop funding if Del-

AWARE were made eligible under the donor-option program." (The

Philadelphia Inquirer, Front Page, Friday, July 26, 1985.)

October 1985 - A emergency evacuation drill turned into a

serious incident when Unit-2 reactor's water level dropped.

October 1985 - PECO is fined by the Occupational Safety and Health

Administration (OSHA) for safety violations leading to the death of

an employee.

December 1985 - An INPO study (as reported by The Nuclear Monitor)

concluded that PECO's performance continued to decline. A subsequent

letter written in January by Zack Pate, President of INPO, to PECO

Chairman John Everett, said "standards of performance at the station are

unacceptably low."

Problems were identified in operations and maintenance, radiological

protection, material condition and housekeeping. INPO also identified

several non-licensed operators reading unauthorized materials. A total of

431 shortfalls were identified; 141 involved personnel performance. Pate

noted,", and "we ... have considerable concern that the station's

substandard radiological control practices may lead to the spread of

contamination off-site, or some other serious radiological event.

Continued on the next page...

Pate concluded, "From my assessment, this pattern will not change, and

personnel performance at Peach Bottom will not improve, until you

personally acknowledge the need and communicate the need, for real

change to your organization."

- February 1, 1986 to May 31, 1987 - The SALP for this period

indicated PECO's performance was "unacceptable" because of the

operators' inattentiveness and management's "inability to identify and

correct operator conduct in other areas."

Among the incidents cited by the NRC: security guards were

overworked, and one guard was found asleep on the job; 36,000

gallons of "mildly radioactive water" leaked into the

Susquehanna River; PECO mislaid data on radioactive waste

classification causing misclassification of a waste shipment; at the turbine

building on March 4, 1987, Unit 3 a major fire occurred at the

maintenance cage.

March 1986 - A checking system was bypassed and automatic backups

were bypassed by a supervisor during an inappropriate withdrawal of a

control rod from the reactor core.

April 1986 - An explosion and fire occurred at the plant's

substation for emergency power.

June 1986 - The NRC's annual report concluded that Peach

Bottom was "operated by well qualified individuals with a positive

attitude toward their positions for nuclear safety."

June 1986 - Unit-2 was shut down when a cooling system pipe sprang

a leak.

June 11, 1986 - A $200,000 fine for failing to pay attention to detail

was issued. The incident involved the withdrawal of control rods. A highlevel,

NRC administrator noted that these violations indicated a continued

"pattern of inattention to detail" and "a general complacent attitude." The

original fine was set at a $100,000, but doubled because of PE's history. In

addition, the NRC reported 17 violations.

July 16, 1986 - While testifying before Congressman Markey's

Committee, the NRC revealed that Peach Bottom was one of the 10 most

hazardous plants in the country. The underlying reason appeared to

be that PECO's attention was focused on the construction and startup of

Limerick, rather than the safe operation of Peach Bottom.

August 1986 - The NRC reported that there were 26 cracks in Peach

Bottom's two operating reactors (Units 2 and 3).

December, 1986 - The NRC reported that a health physicist was

illegally fired for whistleblowing.

February 18, 1987 - An NRC study said Peach Bottom's reactors

were more likely to release radiation in the event of a core-melt

accident.

March 4, 1987 - At the turbine building at Unit 3 a major fire

occurred at the maintenance cage.

The NRC identified several precursor problems with fire protection

on the following dates: April 10, May 30 and November 1, 1985. Another

related problem was documented on January 19, 1990.

March 15, 1987 - The NRC levied a $50,000 against PECO for

illegally dismissing a worker who was exposed to radioactive gas.

March 31, 1987 - Peach Bottom was indefinitely

shutdown. Operators were found sleeping on the job,

playing video games, engaging in rubber band and paper

ball fights, and reading unauthorized material.

May 1987 - The NRC reported that areas of high radioactivity were

not properly marked.

May 1987 - An NRC inspection report revealed 33 operator errors in

the past two years as well as cases of operator inattention and poor

reaction.

July 15, 1987 - Senior Health Physics Technician, George Fields, filed

a lawsuit against PECO for exposing him to dangerous levels of

radioactive gas.

September 1987 - An INPO evaluation ranked the plant in the lowest

category.

September 30, 1987 - A contractor employee attempted to enter a

protected site while intoxicated. Later cocaine was found in the parking

lot and in the guard's bathroom.

October 1987 - An INPO visit (as reported by The Nuclear Monitor)

found that since shutdown, "little clearly demonstrable action has

been taken regarding corporate management's accountability for

conditions at the station."

"Control of drawings, procedures, and other documents used by

operations personnel was identified as a problem at Peach Bottom ... in

1980. During the recent plant evaluation, 22 of 23 drawings reviewed in

the radwaste control room were out of date by as many as 15 revisions.

Outdated or unapproved drawings and procedures were also noted at

various locations in the turbine building and the auxiliary room."

"[T] here were more than 6,000 open maintenance requests, 300

outstanding money tickets (minor maintenance requests), and 1,200

additional items requiring maintenance on various lists ... 586 preventive

maintenance activities ... have been outstanding since June 1986."

October 5, 1987 - A loss of Power at Unit-3 resulted in a containment

isolation and a loss of shutdown cooling.

October 8, 1987 - The NRC deferred a review of PECO's reorganization

plan because of their failure to address corporate weaknesses.

October 9, 1987 - Philadelphia Electric announced a corporate

reorganization plan.

October 29, 1987 - The forced shutdown is costing Philadelphia

Electric an additional $5 million a month for replacement electricity.

("Patriot News".)

November, 1987 - A report published by Public Citizen revealed

that $400 million was spent on repairs at Peach Bottom between

1981 and 1985. This amount was the highest expended at any of

the nation's nuclear power plants.

November, 1987 - The FBI discovered a drug distribution ring at

Peach Bottom.(For more details see: January 8, 1988; February, 1988;

May 2, 1988; November, 1989; and, May 10, 1999.)

January 8, 1988 - A maintenance sub-foreman pleaded guilty to

involvement in a conspiracy to distribute methamphetamine. He is

one of six who were indicted last year in a conspiracy to distribute

methamphetamine. (For more details see: November, 1987; May 2,

1988; and November, 1989.)

January 11, 1988 - INPO President Zack Pate strongly criticized

Philadelphia Electric's management and their revised

reorganization plan.

Pate noted that, "The fundamental approach to nuclear operational

management at Philadelphia Electric Company has not changed and is

unlikely to change noticeably in the foreseeable future." He added, "success

ultimately depends on the individual managers in key line positions. Since

for the most part, the same managers who have been ineffective in this

area for years are in the key line positions in the new organization,

substantial improvement is unlikely." Pate concluded, "Major changes in

the corporate culture at PECO are required. The recently announced

reorganization plan will not achieve this" (The Nuclear Monitor, February

22, 1988, pp.1-2).

January 26, 1988 - Governor Robert P. Casey formally petitioned the

NRC for public hearings on PECO's management.

January 27, 1988 - PECO reportedly lost $58 million due to the NRC's

shutdown of Peach Bottom. Earnings per share were shaved from $2.60 a

share in 1986 to $2.33.

February 3, 1988 - John H. Austin resigned as president of PE after a

unusually critical report by the Institute of Nuclear Power Operations

(INPO) was published. The report asserted that Peach Bottom "was an

embarrassment to the industry and to the nation." Zack T. Pate,

president of INPO, added, "The grossly unprofessional behavior by a

wide range of shift personnel ... reflects a major breakdown in the

management of a nuclear facility."

February, 1988 - The PUC ordered PE to reduce rates by a $37 million

a year until Peach Bottom is allowed to restart.

February, 1988 - Four PECO employees were indicted for allegedly

distributing drugs at Peach Bottom. PECO maintained that the workers

were not working in areas affecting safety. (For more details see:

November, 1987; January 8, 1988; May 2, 1988; November, 1989; and,

May 10, 1999)

February 9, 1988 - In a editorial, The Patriot News concluded: "PECO's

management failed in that basic responsibility to the company's

stockholders, to the federal regulations they are required to abide by and

the public that was put at risk by this slipshod performance."

March 17, 1988 - PE officials acknowledged that the plant will not be

ready for restart until the "...fall frame time." This prediction would mean

that the plant would be shut down for "at last 18 months, costing the

company $125 million, based on its current rate of expenditures for

replacement power and a penalty imposed by the state Public Utility

Commission" (The Patriot News, March 17, 1988, p.B-9).

March 29, 1988 - The Public Citizen's Critical Mass Energy Project

rated Peach Bottom as one of the poorest rated plants in the country based

on the following criteria: "average lifetime operating efficiency; 1987

operating efficiency; average operating and maintenance costs during

1985 and 1986; average capital additions costs from 1982 to 1986; most

recent SALP ratings; number of scrams during 1985 and 1986; average

annual fines from 1985 to 1987; worker exposures from 1984 through

1986; LERs in 1985 and 1986; potential accident consequences derived

through the CRAC-2 computer code" (The Nuclear Monitor, May 2, 1988,

p.6).

An NRC's evaluation of the plant's management performance rated

Peach Bottom as the eighth worst in the country.

April 7, 1988 - The Janny Montgomery Scott basic report on

Philadelphia Electric noted that PE still faces many hurdles, including:

"...further intense scrutiny from the regulatory commissions, and the

uncertainty of future rate relief. Accordingly, the stock remains suitable

primarily for investors willing to assume above-average risk." And,

"Certainly, the extensive nature of the management reorganization will

require time to evolve, but many deep-rooted problems such as those

initially developed at Peach Bottom are corrected now."

April 13, 1988 - J. Lee Everett "retired" as Chairman and Chief

Executive Officer of Philadelphia Electric as a direct result of the harsh

criticism from a January 12, 1988 report released by the Institute of

Nuclear Power Operations (Refer to February 3, 1988).

May, 1988 - Bessie Howard filed a complaint with the United States

Department of Labor alleging that she was fired "in retaliation for her

identification of safety problems relating to security at Peach

Bottom." Beginning on January 24, 1988, Mrs. Howard reported that

another security guard was sleeping on the job. She continued to report

the matter until she was fired On March 16, 1988, by Burns Security, the

security contractor for Peach Bottom. She was classified "status nine" and

prohibited from working at other nuclear power plants or government

facilities.

- A report issued by the NRC indicated "that security personnel were

forced to work excessively long hours, sometimes up to 12 hour

shifts; were not given meal breaks, and were required to remain

at posts for extended periods of time without being rotated to

other posts, a violation of NRC regulations" (York Daily Record, May

1988).

May 2, 1988 - Four Peach Bottom employees were charged with

conspiracy to distribute methamphetamine at the plant and

elsewhere. Thirteen people, most of whom work at Peach Bottom, have

been charged with drug-trafficking as a result of an FBI investigation. (For

more details see: November, 1987; January 8, 1988; February, 1988;

November, 1989; and May 10, 1999.)

Spring 1988 - A cot for sleeping on the job was removed from an

area located near the control room, and the NRC acknowledged knowing of

its presence prior to its removal.

June 6, 1988 - The NRC warned that the "effort to make sure the

Peach Bottom nuclear power plant is run safely is by no means a

sure thing " (Centre Daily News, June 1, 1988, A-6).

June 16, 1988 - The General Counsel to the Governor of Pennsylvania

submitted comments on the Revised Plan for Restart of Peach Bottom

Atomic Power Station and the Actions of Philadelphia Electric Company

Leading Up to and Succeeding the March 31, 1987 Shutdown Order of the

Nuclear Regulatory Commission.

Counsel noted, "The plan on the whole remains too general to

permit proper evaluation. Some of the most crucial areas, for example,

the responsibility for individual operators and those managers who are

retained for previous misconduct and the justifications for their retention,

remain undisclosed. Certain basic problems, such as drug abuse and

previous sanctions against whistleblowers, are either not addressed at all

or are insufficiently addressed. Independent assessment organizations need

even greater independence and must satisfactorily demonstrate reanalysis

of problem reports (such as Significant Operating Events and vendor

reports) that may have triggered inadequate responses over the last few

years. Finally, and most importantly, the reforms generally proposed

must be reduced to specific, clear, verifiable commitments and proper

avenues outlined for verification."

July 27, 1988 - Public Service Enterprise Group Incorporated and its

subsidiary Public Service Electric and Gas Company filed and action in the

United States District Court to recover damages resulting for the

NRC's shutdown of Peach Bottom. On the same in the same court,

Atlantic City Electric Company and Delmarva Power and Light Company

filed similar suits against Philadelphia Electric. The suits allege that PECO

breached its contract under the Owners Agreement. Several tort claims

were also filed, however no dollar amounts were specified. (Based on

information from Philadelphia Electric Company's "Report to Shareholders

Third Quarter 1988.") (See April 4, 1992 for settlement agreement.)

August, 1988 - Peach Bottom's security contractor was replaced

due to incompetence.

August 11, 1988 - The NRC proposed fining PECO $1.25 million for

"management problems that resulted in a forced shutdown of the

company's Peach Bottom nuclear plant." In addition, the NRC proposed

fining 33 reactor operators for sleeping on the job, playing video

games, engaging in spit ball battles, and other unprofessional

activities. Fines of $500 to $1,000 were recommended. PECO

spokesperson Williams Jones disclosed that the company "has lost more

than $90 million since the NRC ordered Peach Bottom shutdown..."

(Patriot News, August 12, 1988).

August 17, 1988 - Joseph Rhodes, Jr., a member of the Pennsylvania

Public Utility Commission, suggested that a deal between PECO and the

NRC might have been made in order to get Peach Bottom back on line. In

letters to NRC Chairman Lando Zech and PECO CEO Joseph Paquette, Jr.,

Rhodes stated, "One could draw the conclusion that by announcing these

fines, the NRC has cleared the way for PECO to receive expedited approval

of its Peach Bottom restart plan"(Patriot News, August 17, 1988).

September 2, 1988 - An electrician, working in the low- level

radioactive area, " ... fell from scaffolding into a puddle of radioactive

water...suffering slight contamination..." (The Patriot News, September 2,

1988).

September 15, 1988 - NRC Chairman Lando Zech told senior

management officials of PECO, "I'm not going to accept what you say

today and be anywhere near ready to authorize this plant." Zech

noted, "Your operators certainly made mistakes, no question about that.

Your corporate management problems are just as serious." Zech added,

"The fact that we have a situation like this existing at any plant in the

country is very serious. We're responsible to the American people. We can't

have plants with this much inattentiveness to anything."

Continued on the next page...

William Russell, regional administrator, told plant officials that

unacceptable levels of contamination exist in three pump rooms that

are part of Peach Bottom's water cleanup system. He said the radiation in

those locations is "some of the worst I've seen" (The Evening News,

September 15, 1988, B 3.)

September 23, 1988 - The Board of Directors voted to take no action to

prevent the progress of shareholder lawsuits against former chairman and

CEO, James L. Everett, III, and former President and CEO, John H. Austin,

Jr., "for claims alleging mismanagement which resulted in the

shutdown..." of Peach Bottom (Philadelphia Electric Company, Report to

the Shareholders, Fourth Quarter, 1988.)

September 26, 1988 - Governor Casey, through the Pennsylvania

Department of Environmental Resources (Pa DER), ordered PECO and

INPO to release files on recent investigations of the plant. Governor Casey

noted, "We made it clear there were certain kinds of information we needed

to evaluate our concerns, but after months of being unable to persuade

PECO to provide us with that information on its own, we had to go ahead

and issue these orders." ( Philadelphia Inquirer, September 27, 1988.)

September 27, 1988 - A jury awarded $130,000 to four pipe

fitters who claimed they have health problems as a result of being

exposed to asbestos at several construction sites including Peach

Bottom, Three Mile Island and Glatfelter paper mill.

September 28, 1988 - Senator William Lincoln of Fayette announced

that hearings should be required before a Peach Bottom restart.

October 14, 1988 - PE appealed the Pa DER order to give the Casey

administration access to internal documents relating to restarting Peach

Bottom.

October 19, 1988 - INPO "provided observations on its corporate

evaluation conducted in October and on its plant evaluation conducted in

September" (Philadelphia Electric Company, Report to the Shareholders,

Fourth Quarter, 1988.)

INPO noted "that the operators needed additional simulator training to

properly respond to some plant events, that management and shift

supervision must take more effective action to correct significant

operational and administrative problems, that administrative provisions

must be upgraded to better help control room operators readily and

accurately determine plant status, and that improvements are needed in

communicating and assessing performance standards."

October 21, 1988 - PECO announced a revision in their restart

schedule. The projected date for restart was pushed back to the second

quarter in 1989.

October 27, 1988 - A recent safety evaluation conducted by the NRC

was favorable for restart, according to PECO spokesman Neil McDermott.

"What it [the report] is saying is that our plan addresses the problems

which led to the shutdown, and that actions laid out in the plan are

appropriate to correct those root causes." He added, "Now, of course, the

NRC will continue to monitor the effectiveness of the implementation"

(The Patriot News, October 22, 1988, B 9.)

November 17, 1988 - The NRC fined PECO $50,000 because

security guards were found sleeping on the job, inattentive duty

and improperly posted. The NRC also noted that "a key that could have

unlocked doors to a security area was issued to a unauthorized employee,

couldn't be found and officials didn't do anything about it once they

discovered it was missing." William T. Russell, NRC regional

administrator, noted, "The improvements made to date were not effective

in precluding the occurrence of the violations" (The Patriot News,

November 17, 1988, B 2.)

January 1989 - The state of Maryland published a report of

radioactive contamination of the Chesapeake Bay due to to

emissions from Peach Bottom. (Note: The city of Baltimore gets 250,000

gallons of drinking water per day from the Susquehanna River.)

January 12, 1989 - Admiral James D. Watkins, a member of

Philadelphia Electric's Board of Directors, was nominated for the post of

Secretary of the Department of Energy.

February 1, 1989 - The NRC staff recommended that nuclear power

plants that utilize the Mark 1 containment shell, modify the structure

to reduce the risk of failure during a serious accident. PECO said it

would make the $2 to $5 million changes only if the Nuclear Regulatory

Commission makes the modifications a requirement. This is the second

time in two years that the NRC staff has advised the Commission to make

changes to the Mark 1 containment structure.

February 8, 1989 - The NRC announced that despite

improvements at Peach Bottom, a restart vote will not take place

until April, 1989.

February 18, 1989 - The NRC's Integrated Assessment Team's

Inspection announced that PECO was close to restarting Peach Bottom.

February 28, 1989 - The Commonwealth of Pennsylvania and

Philadelphia Electric concluded an agreement that would give the

Commonwealth access to confidential material and allow the state to

monitor PECO's operation of Peach Bottom. The agreement was not an

endorsement for restarting Peach Bottom.

February 28, 1989 - The Lancaster New Era declared in an editorial

on restart that, "While the company claims it sincerely has reformed, we

have the overriding impression that reopening the plant, not safety, is the

bottom line for the plant operator, Philadelphia Electric Co."

April 21, 1989 - By a 3-0 vote, the NRC approved the restart of Peach

Bottom. PECO spokesman Bill Jones calculated that the shutdown cost

Philadelphia Electric $300 million. (Patriot News, April 21, 1989, B-3.)

"Whistleblower" W. Allan Young, who was fired from Peach Bottom

after raising concerns about workers being exposed to high levels of

radiation, said in an open letter to the NRC, that the same people who

fired him and prevented his rehiring at the plant, are still there. Young

told WITF-TV, "They have idiots running that plant."

April 27, 1989 - "An unplanned shutdown was made to repair three

malfunctioning intermediate range monitors (IRM) during reactor

startup" (SALP 50-277/88-99; 278/88-99.)

April 28, 1989 - Peach Bottom began its ascent towards full power.

May 11, 1989 - "An unplanned shutdown was made to replace a

malfunctioning safety relief valve (SRV) which was slow to reclose" (SALP

50-277/88-99; 278/88-99.)

May 14, 1989 - The reactor was taken to subcriticality due to problems

with the the electro-hydraulic control (EHC) system (SALP 50-277/88-99;

278/88-99.)

May 19, 1989 - Peach Bottom was shut down due to mechanical

problems. Unit 2 "automatically scrammed from 20% power. The cause of

the scram was a failed 'three element/single element control switch in the

feedwater system" (SALP 50-277/88- 99; 278/88-99.)

May 22, 1989 - "A malfunction in the offgas recombiner system caused

the licensee to shutdown the turbine generator and reduce power to 5%"

(SALP 50-277/88-99; 278/88-99.)

May 31, 1989 - Peach Bottom was ranked the third worst nuclear

power plant in the nation according to a report released by the

consumer group Public Citizen. The report, "Nuclear Lemons: An

Assessment of America's Worst Commercial Reactors," was based on

information obtained from the government and nuclear industry.

June, 1989 - Although the NRC revised its its list of troubled reactors,

Philadelphia Electric's Peach Bottom reactors remained on the list.

June 21, 1989 - The NRC released a report on Mark 1 containment

buildings entitled "Severe Accident Risks: An Assessment for Five

U.S. Nuclear Plants." The NRC's six-member panel were evenly divided

as to whether the Mark 1 containment would be breached during a serious

accident. Accordingly, "The NRC decided not to order immediate changes

in the Mark 1 containment". (The Patriot News, July 21, 1989, B3.) Yet

half of the panel stated "with near certainty" the Peach Bottom's

containment structure would fail during a core melt accident.

July 21, 1989 - At Peach Bottom 2: "An automatic reactor scram on

main steam isolation valve (MSIV) closure occurred when troubleshooting

activities in an electro-hydraulic control cabinet caused a false indication

of high reactor pressure"(NRC SALP 50-277/89-99; 278/89-99,p.3.)

August, 1989 - PECO "operated Unit 2 at power for about 32 hours

with the emergency service water system inoperable." PECO was cited and

paid a civil penalty on August 15, 1990.(See February, 1990 for related

incident.) (NRC IR 50-277/92-09 and 50-278/92-09.)

August 5, 1989 - PECO reached an agreement with the Public Utility

Commission "not to charge customers for $24.3 million in costs incurred

by the company when the Peach Bottom nuclear power plant was shut

down under a federal order" (Patriot-News, August 4, 1989, B-6.)

However, PECO is seeking to "recover" $107 million from its customers

through a rate increase.

September, 1989- The NRC released a SALP report indicating

weaknesses "...in the performance of and support for some engineering

projects, corporate technical assessment activities and management

support for health physics training programs and technical facilities"

(Annual Report 1989, p.13.)

September 15, 1989 - The Pennsylvania Superior Court reversed

a lower court's decision dismissing charges by George Field

against the Philadelphia Electric Company. Field, a health- physics

technician, alleged that PECO directly released radiation on him to avoid

shutting the plant down. The three judge panel concluded:

We can visualize no conduct more outrageous in character, so

extreme in degree, that went beyond all possible bounds of decency

and to be regarded as atrocious and utterly intolerable in a civilized

community, than to vent highly radioactive steam upon an

employee. Furthermore, this was an intentional act. They elected to

do this to him and then attempted to conceal the resulting situation

The three judge panel remanded the case back to York County Common

Pleas Court. Field is seeking $5.2 million in damages.

(The Philadelphia Inquirer, September 15, 1989, 3-B.)

September 19, 1989 - In a report entitled Nuclear Legacy: An

Overview of the Places, Problems and Politics of Radioactive Waste in the

United States, (Public Citizen September 1989), Peach Bottom was

identified as hosting one the largest irradiated fuel pool

inventories in the nation. (Peach Bottom-2 was ranked seventh and

Peach Bottom-3 was ranked eighth.) The combined volume of irradiated

fuel being stored at Peach Bottom is 299.8 cubic meters. The material

stored in these pools is classified as high-level reactor waste.

October 5, 1989 - The NRC lifted its shutdown order on Peach

Bottom. (The order was enacted on March 31, 1987.) This action allows

Unit-3 to restart immediately. (Unit-2 has been operating since April,

1989, while the shutdown order was in effect.) The order also reduces the

"strict" monitoring presence of the NRC at Peach Bottom. "The total cost of

the shutdown was about $250,000 million, including $168 million for

replacement power and a $46 million fine imposed by the state and Public

Utility Commission" (Patriot News, October 6, 1989, B-6.)

October 5, 1989 - An automatic scram occurred at Unit 2 due to

equipment failure. The plant was at 100% power when "... an outboard

MSIV closed during surveillance testing, causing a pressure spike and a

high high flux reactor scram" (NRC SALP 50-277/89-99;278/89-89, p.4.)

October 5-10, 1989 - Peach Bottom shut down due to mechanical

problems.

November, 1989 - A former PECO employee was convicted by a

federal jury of possessing methamphetamine at Peach Bottom in

1985 and 1986. (For more details see: November, 1987; January 8, 1988;

February, 1988; and, May 2, 1988.)

November 26, 1989 - An unplanned shutdown at Unit 2 resulted

from equipment failure and design weakness.The plant was operating at

full power when "an unplanned shutdown was made to repair an

unisolable steam leak outside containment emanating from the RCIC

injection check valve hinge pin picking" (NRC SALP 50-277/89-99;

278/89-99, p.4.)

Precursor RCIC problems were identifed by the NRC on the

follwoing dates: December 10, 1982, March 8 and June 28, 1984, and

August 14, 1985.

December 11, 1989 - PECO restarted Unit-3 which was shutdown

by the NRC on March 31, 1987. The company has estimated the total

cost of the shutdown now exceeds $214 million, including monies spent for

replacement power and a rate penalty levied by the Pennsylvania Public

Utility Commission (Patriot News, December 13, 1989.)

December 20, 1989 - Unit-2 experienced an "unusual event" and was

shutdown. The plant was automatically shutdown from 100% power "after

a technician tested a power monitor, according to officials of Philadelphia

Electric Co." (Patriot News, December 21, 1989.)

December 27, 1989 - Peach Bottom 2 restarted after shutdown.

January 8, 1990 - The Patriot News reported, "Philadelphia Electric

Co. conducted psychological screenings of control-room operators at its

Peach Bottom nuclear power plant to determine how many could be

retrained after the plant was closed down by the Nuclear Regulatory

Commission in 1987" (Patriot News, January 8, 1990, C3.)

The behavior-modification and rehabilitation program, "People: The

Foundation of Excellence," was conducted by the psychologists' firm of

Rohrer, Hibler & Replogle. Twenty-four out of the 36 control-room

operators at the time of the shutdown entered the program. In addition,

"10 of the remaining 12 were demoted and reassigned. Of the other two,

one retired and one resigned. None of the five shift supervisors were

considered for retraining, and were among the group demoted and

reassigned" "Patriot,C3)

Continued on the next page...

In a memo from Julius J. Persensky, a section chief in the NRC's

Human Factors Assessment Branch, Mr. Persensky noted the program

was of limited value and operators still believe "that their previous

behavior was safe." Persensky's memo also noted that Rohrer, Hibler &

Replogle found the operators to be: a depressed, powerless, angry,

humiliated and victimized group who didn't think they were doing wrong;

practical as opposed to theoretical; open, candid and forthright; sheltered,

narrow, parochial and naive; and, loyal to the organization, their

profession and the company. According to Rohrer, Hibler & Replogle, up to

ten people in may have to retake the program. (Patriot, C3.)

January 27, 1990 - Unit 2 was shutdown again due to equipment

failure and design weakness. The plant was shutdown to "repair an

unisolable leak outside containment on a "B" reactor feedwater pump

discharge flow instrument line" (see November 26, 1989 for a related

incident) (NRC SALP 50-277/89-99;278/89-99, p.4.)

January 28, 1990 - Unit 3 was forced into, "A fast power reduction

and manual reactor scram were initiated when an electro-hydraulic

control system fluid leak developed. The leak was caused by a failed sealing

"O" ring ( NRC SALP 50-277/89-99; 278/89-99, p.4.) The plant was

operating at 100% power.

February, 1990 - The emergency service water system "became

inoperable due to improper restoration from maintenance activities." (See

August 1989 for related incident.) (NRC IR 50-277/92-09 and 50-

278/92-09.)

March 6, 1990 - Unit 3 was shut down due to a "mechanical problem

with the system's generator, officials said. Unit 2 had been shut down last

week for maintenance" (York Daily Record, March 7, 1990.) However, an

inspection report compiled by the NRC stated that "equipment failure

complicated by inadequate surveillance procedures" resulted in an

automatic scram. The event was caused when "the main turbine tripped

at a reactor power of 35% due to A loss of main generating stator cooling"

(NRC SALP, 50-279/89-99;278/88-99, p.5.)

March 31, 1990 - In PECO's Report to Shareholders First Quarter 1990,

the "Company reported a loss of $84 million, equivalent to 40 cents per

share, compared with earnings of $118.9 million or 57 cents per share for

the same period a year ago when 2.6 percent fewer shares were

outstanding."

April 11, 1990 - Peach Bottom's Unit 2 and Unit 3 reactors were rated

third and fourth worst in the nation in terms of worker exposures,

according to a report released by Public Citizen's energy policy group. The

report was based on data obtained from the NRC.

April 21, 1990 - Peach Bottom 2 was "taken off line due to

vibrations in the unit's generator exciter" (York Daily Record, May 1,

1990.) Personnel error, procedure weakness and equipment failure

contributed to the shutdown.

April 23, 1990 - In a letter to Philadelphia Electric Shareholders,

Joseph Paquette, Chairman and CEO, announced, "... the Company's Board

of Directors voted to reduce the Company's quarterly dividend from $.55

per share to $.30 per share per share effective with the payment for the

second quarter of 1990 to be made June 29, 1990." This action was linked

to a rate request regarding the costs of operating and owning Limerick.

- In the Report to Shareholders for the Third Quarter 1990,

Philadelphia Electric reported reaching a settlement "in the shareholders'

derivative suit brought by certain shareholders against the Company's

former Chairman and former President in connection with the events

leading to the shutdown....Under the terms of a settlement agreement, two

of the Company's director and Officer liability insurance carriers paid

approximately $34.5 million. The settlement became final on October 30,

1990. The plaintiffs' recovery, less $6.5 million for their attorneys' fees

and expenses were paid to the Company on November 1."

However, In PECO's annual statement, the company admitted, "The

penalties associated with the [Peach Bottom's] shutdown for 1989

amounted to 23 cents per share, compared to 25 cents per share for 1988"

(Annual Report 1989, p.14).

In addition, "The Company did not request recovery of any Peach

Bottom replacement power costs incurred solely as a result of the NRC's

shutdown order. In 1989, replacement power costs attributable to the

shutdown order were approximately $57 million , representing a

reduction in common stock earnings of 17 cents per share"

(Annual Report, p.21.)

May 11, 1990 - "...instrument and controls technicians replacing a

voltmeter on the '3B' battery charger caused a DC electrical system

voltage transient" (NRC IR 50-277/92-09 and 50-278/92-09.)

June 15, 1990 - The Public Utility Commission (PUC) ruled that

Philadelphia Electric had to refund to its customers $15 million. "The PUC

ruled that PECO kept sloppy records, did not use enough competitive

bidding and did not bid projects frequently enough" (Patriot News, June

15, 1990.)

June 26, 1990 - The Pennsylvania Public Utilities Commission

(PUC) released its twelfth annual report on utility consumer complaints to

the PUC's Bureau of Consumer Services. The report noted that PECO was

one of the companies whose overall performance "was worse than that of

other companies" and "would benefit both from a critical review of their

own operations and from attempting to emulate the operations of the

companies which performed best."

July 18, 1990 - The NRC fined PECO $75,000 for violations of

technical specifications involving the "plant's emergency service water

system, a support system designed to cool safety equipment, other than

the reactors, at Peach Bottom's Units 2 and 3" (The Patriot, July 18, 1990,

B 5.)

July 28, 1990 - Philadelphia Electric declared an unusual event

from "5:38 am to 6 am because of a momentary increase in radiation

levels in an internal gas-filtering system" (Patriot News, July 28, 1990, A

3.) Radioactive gas was released into the environment for ten minutes.

August 15, 1990 - PECO paid a civil fine to the NRC for an

August, 1989 incident involving the emergency service water system.

(Also see February, 1990.)

August 16, 1990 - In NRC inspections from July 1,1989 to May 31,

1990, Peach Bottom 2 "experienced six unplanned shutdowns because of

personnel errors or equipment failures, while the Unit 3 reactor had two

shutdowns " (Philadelphia Inquirer August 16, 1990, 17 D).

September 11, 1990 - PECO "discovered that indications derived

from Unit 3 reactor water level transmitters...were abnormally high

when compared to actual reactor water level" (NRC IR 50-277/92-13 and

50-278/92-13.) (See March 26 and 27, 1992 and July 26, 1992 for

related incidents.)

December 1, 1990 - In Philadelphia Electric's Report to

Shareholders Third Quarter 1990,PECO announced: "For the three months

ended September 30, 1990, the Company reported a loss of $8 million, or 4

cents per share ....Earnings for the twelve months ended September 30,

1990 were 53 cents per share, $1.68 under the earnings of the previous

twelve month period."

February 1, 1991 - In PECO's Annual Report 1990, the company

noted that earnings per share plummeted by a $1.78. Operating and

maintenance costs rose by $406 million or 38%.

February 11, 1991 - "A contractor working inside the dormant

Unit 2...took an 8-foot fall and was flown to York Hospital with slight

contamination to his forehead." Neil McDermott, a company spokesman

for PECO, said: "They resolved it by, (the contamination), well, soap and

water" (Patriot, February 11, 1991.)

February 12, 1991 - A, "Unit 2 primary containment isolation

system (PCIS) and standby gas treatment system (SGTS) initiated (9:10

am) due to an electrical ground. "The event was not detected by the plant

operators until about 10:00 am, because related annunciators had been

removed from service for outage work" (NRC inspection reports 50-

277/91-08; 50-278/91-08, p.2.)

February 20, 1991 - At about 1:10 pm, a full Unit 2 reactor scram

occurred due to inadequate blocking. "The unit was in refueling at the

time with all control rods inserted" (See related incident on February 21,

1991)(NRC inspections 50-277/91-08;50-278/91-08, p.2.)

February 21, 1991 - Inadequate blocking caused a loss of shutdown

cooling. The "isolation occurred when an auxiliary operator (AO)

inadvertently grounded a lead in the control room panel while applying a

blocking permit" (See related incident on February 20, 1991) (NRC

inspections 50-277/91-08;50-278/91-08, p.3.)

February 21, 1991 - At 10:00 pm at Unit 2, fuel bundles were

misplaced during a core reload. "An investigation revealed that the bundle

had been erroneously loaded ...at 1:47 of the same day" (See related

incidents on February 21-22, 1991)(NRC inspections 50-277/91-08; 50-

278/91-08, p.4.)

February 22, 1991 - A fuel bundle at Unit 2, at a separate location

from the previous day's error, was "incorrectly loaded" at 1:15 pm. The

errors was not found until 6:00 am on February 24, 1991. Contributing to

this error Poor CCTAS legibility" and "less than adequate

communications."

On the same day a third and fourth error occurred!

"The third error was identified at about 3:00 pm....Fuel movement

was suspended and the core and spent fuel pool (SFP) were inspected,

leading to the discovery of fourth error" (See February 21 1991 for a

related incident) (NRC inspections 50-277/-91-08; 50-278/91-08.)

February 23, 1991 - The refueling moderator temperature was

exceeded. "The lower moderator's temperature results in the addition of

positive reactivity, and a decrease in shutdown margin....Fuel reload was

halted..." (NRC inspection reports 50-277/91-08;50-278/91-08, p.6.)

February 25, 1991 - Unit was at 100% power when "a high

pressure coolant injection (HPCI) was declared inoperable when the

mechanical overspeed trip (MOTD) did not operate as designed during

performance of a routine surveillance test" (NRC inspection reports 50-

279/1-08/50-278/91-08, p.3.) (For related events see: May 18 and 21,

1991; July 15-19, 1991; August 25, 1991; and, October 16, 1991.)

March 21, 1991 - PECO "found four normally locked open unit 2

valves unlocked. Two of these valves were also closed" (NRC inspection

reports 50-277/91-13;50-278/91-13, p.11.)

April 1-5, 1991 - The NRC issued a Notice of Violation. "The

violation is of concern because of the possible incompatibility of the

insulation with materials it is in contact with and the fact that it may

compromise fire loadings and propagation potentials" (NRC inspections 50-

277/91-14 and 50-278/91-14.)

April 7, 1991 - The Chief Rector Operator discovered that the

Technical Specifications surveillance requirement to log Unit 2's reactor

vessel heat up rate had not been performed . ( NRC inspections 50-277/91-

13;50-278/91-13, pp. 2-3.)

April 10-11, 1991 - The Unit 3 high pressure coolant injection

system failed several times.

April 15, 1991 - During maintenance testing it was discovered

that "valves were reinstalled in the wrong direction following the current

valve refurbishment" (NRC inspection reports 50-277/91-13/50-278/91-

13, p. 5.)

April 22, 1991 - "...a fault developed in one of the conductors

connecting the secondary side of the # 2 Emergency Auxiliary (2EA)

transfer to the safety and non-safety related 4 KV busses" (NRC inspection

reports 50-277/91-13;50-278/91-13, p.7.)

April 23, 1991 - At Unit 2 "reactor power was decreased, the mode

switch was placed in startup and power was held at 5% to replace cable on

an emergency transformer when its insulation was found to be shorted"

(NRC inspection reports 50-277/91-16 and 50-278/91-16, Details.)

April 25, 1991 - Peach Bottom 2 was rated the third worst

nuclear reactor in the county. Peach Bottom 2 and 3 were tired for

seventh worst rate of worker exposure to radiation. (Public Citizen,

Nuclear Lemons: An Assessment of America's Worst Commercial Nuclear

Power Plants.)

May 2, 1991 - "Due to further degradation of emergency

transformer cable insulation the unit (2) was shut down on may 2 to

replace the cables" (NRC inspection reports 50-277/91-16 and 50-278/91-

16, Details.)(See July 4, 1992 for a related incident.)

May 9, 1991 - The Unit 3 reactor experienced "an unexpected

isolation of the reactor water cleanup (RWCU) system occurred when

technicians placed a jumper in an incorrect location" (NRC inspections 50-

277/91-16 and 50-278/91-16, p.2.)

May 13-20, 1991 - An NRC inspection noted that: "During the

1991 Unit 2 refueling outage, leaks in the Unit 3 Offgas System allowed

noble gas to be released to many areas of the plant"(NRC inspection reports

50-277/91-17 and 50-278/91-17, p.3.)

May 15, 1991 - During the performance of a surveillance test at

Unit 2, "system engineers incorrectly removed fuse DD-29 from panel

20C15 instead of the specified fuse DD-28. Pulling the fuse removed power

from the primary containment isolation system (PCIS) group III inboard

isolation logic, causing the associated components to isolate" (NRC

inspection reports 50-277/91-16 and 50-278/91-16, p.3.)

May 18, 1991 - The Unit 2 high pressure coolant injection (HPCI)

system was made inoperable during fire protection system surveillance

testing. (NRC inspections 50-277/91-16 and 50-278/91-16.) (For related

event see: February 25, 1991; May 21, 1991; June 19, 1991; July 15-19;

August 27, 1991; and, October 16, 1991.)

May 20, 1991 - At Unit 3, "the residual heat removal (RHR) pump

automatically started when technicians incorrectly removed a switch

from the 'test position'" (NRC inspection reports 50-277/91-16 and 50-

278/91-16, p.4.)

May 21, 1991 - During a routine surveillance procedure at Unit 2,

"an unexpected isolation of the HPCI system steam line" occurred (NRC

inspection reports 50-277/91-16 and 50-278/91-16, p.4.) (For related

events see: February 25, 1991; May 18, 1991; June 19, 1991; July 15-19;

August 25, 1991; and, October 16, 1991.)

May 21, 1991 - Both units were affected by the inoperability of the

emergency diesel generator due to unqualified relays. (NRC inspection

reports 50-277/91-16 and 50-278/91-16, pp.5-6.)

May 23, 1991 - Units 2 and 3 were shutdown "due to a belief that

the 4 station Emergency Diesel generators (EDG's) could potentially be

rendered inoperable during design basic events" (Licensee Event Report

50-277 and 50-278.)

May 29, 1991 - Both standby liquid control (SLC) pumps at Unit 3

were rendered inoperable due to high tank temperatures. (NRC inspection

reports 50-277/91-16 and 50-278/91-16.)

June 7, 1991 - Unit 2 was shutdown (tripped) due to inadequate

recirculation pump seal cooling.((NRC inspections 50-277/91-16 and 50-

278/91-16.)

June 15, 1991 - An NRC inspector "found a security guard asleep

on the Unit 2 refuel floor...The guard had been assigned to watch a cask

which had not been opened and searched" (Inspection reports 50-277/91-

20 and 50-278/91-20.)

June 19, 1991 - A Notice of Violation was issued for an incident

which involved the high pressure coolant injection system on May 21,

1991.(See February 25, 1991; May 18 and 21, 1991; and, July 15-19,

1991 for related incidents.)

June 24, 1991 - Unit 2 pressure transmitters were identified as not

being seismically supported."The support for the PT's was mounted on non

seismic floor grating and only one of four anchor bolts was installed"

(Inspection reports 50-277/91-20 and 50-278/91-20.)

June 24-28, 1991 - A Notice of Violation was issued for the

following: "Two instances were identified in which corrective actions taken

by your staff had not adequately resolved deficiencies related to quality

classification of safety-related equipment (Q-List), and control of

measuring and test equipment" (NRC inspection 50-277/91-20 and 50-

278/91-20.)

June 24-28, 1991 - An NRC radiological safety inspection

observed, "Audit findings indicated that, at times, management had

provided poor oversight of program activities. For example, individuals

who failed to perform radiologically sound work were not always held

accountable for their work. Examples of poor quality were observed for

individuals both internal and external to the HP organization" (NRC

inspections 50-277/91-22 and 50-278/91-22)

June 27, 1991 - An unplanned manual scram occurred at Unit 2

due to low condenser vacuum.(NRC inspection reports 50-277/91-20 and

50-278/91-20.)

July 7, 1991 - Unit 3 was scrammed following a trip of the main

generator output breakers. (NRC inspections 50-277/91-20 and 50-

278/91-20.)

July 8-12, 1991 - The NRC staff "...identified several instances of

failure to take effective corrective action in response to previously

identified problems in the surveillance testing area. We are concerned

with this matter because of the time which has elapsed since these

problems were first identified. Management has not developed detailed

plans or goals to improve performance in this area" (NRC inspections 50-

277/91-23 and 50-278/91-23.)

July 10, 1991 - At Unit 3, "licensee technicians inadvertently

caused a trip of the "B" reactor protection system (RPS) motor generator

(MG) set." The secondary containment was also isolated during

troubleshooting. (NRC inspections 50-277/91-21 and 50-278/91-21.)

July 16-17, 1991 - The licensee determined that there was low

emergency water flow to Unit 2's Emergency Diesel Generators and

residual heat removal pumps. "As a result, the Unit 2 RCIC and 'B' loop of

low pressure coolant injection (LPCI) were declared inoperable on July 16

and 17" (NRC inspections 50-277/91-21 and 50-278/91-21.)

July 15-19, 1991 - During an inspection the NRC observed: "...one

of your activities related to the operability of the high pressure coolant

injection (HPCI) system appears to be in violation of NRC requirements..."

(NRC inspections 50-277/91-24 and 50-278/91-24.) (For related events

see: February 25, 1991; May 18 and May 21, 1991; June 19,1991; August

25, 1991, and, October 16, 1991.)

July 18, 1991 - The Unit 2 high pressure coolant injection system

isolated during surveillance testing. (NRC inspections 50-277/91-21 and

50-278/91-21.)

July 24, 1991 - An initiation of a Unit 3 plant shutdown occurred

due to an inoperable DG Auto-start logic. (NRC inspections 50-277/91-21

and 50-278/91-21.)

July 27, 1991 - There was a partial containment isolation at Unit

3 following the failure of a 500 KV disconnect switch.

July 24, 1991 - A letter from the Assistant Associate Director of

FEMA noted: "Twenty-two Areas Requiring Corrective Action were

identified during the [emergency preparedness practice on February 7,

1990] exercise. FEMA's Region III staff will monitor the status of the

corrective actions" (Letter to the NRC from Dennis H. Kwitatkoski.)

July 30- August 1,8 and 22, 1991 - The NRC conducted safety

inspections of emergency preparedness exercises and found: "While no

violations were noted during the inspection, one exercise weakness was

identified. This weakness concerned a significant breakdown in the

communication, distribution, and tracking of scenario data" (NRC

inspections 50-277/91-25 and 50-278/91-25.)

July 31, 1991 - A Notice of Violation was issued for an "event at the

Peach Bottom facility during which you [PECO] overheated the Unit 3

standby liquid control (SLC) solution storage tank" (See May 29, 1991 for

more details) (NRC inspections 50-277/91-16 and 50-278/91-16.)

August 5, 1991 - Unit 2 scrammed at 98% power. "The main

turbine tripped due to high level in the 'D' moisture separator drain tank

(MSDT)" (NRC inspections 50-277/91-27 and 50-278/91-27.)

August 12, 1991 - The NRC revealed that they did not have

current copies of Peach Bottom's Emergency Operating Procedures.

August 25, 1991 - Unit 3 was shutdown due to inoperable room

coolers. PECO "found that both the high pressure coolant injection (HPCI)

and the reactor core isolation cooling (RCIC) system pump component

coolers were inoperable" (NRC inspections 50-277/91-27 and 50-278/91-

27.) (For related incidents see: February 25, 1991; May 18 and 21, 1991;

July 15-19, 1991; and, October 16, 1991.)

August 27, 1991 - Both units were "shutdown following discovery

that two of the four emergency diesel generators (EDG) were inoperable"

(NRC inspections 50-277/91-27 and 50-278/91-27.)

September 8, 1991 - Philadelphia Electric "discovered that the "A"

CAD sample line from the torus was plugged" (NRC inspection 50-277/91-

27 and 50-278/91-27.)

September 12, 1991 - An unusual event was declared when jet

pump components dropped into the spent fuel pool" (NRC inspections 50-

277/91-27 and 50-278/91-27.)

September 17, 18 and 24, 1991 - The control room emergency

ventilation system isolated and transferred to the emergency ventilation

mode" (Another occurrence was reported on October 25, 1991.) (NRC

inspections 50-277/91-27 and 50-278/91-27.)

September 19-20 and 23-24, 1991 - A Notice of Violation was

issued by the NRC. The staff reported: "Of concern to us associated with the

work on RWCU Pump 3B was the failure of your staff to perform an

assessment of the radiological hazards associated with pump components

and subsequent failure to establish appropriate radiological controls for the

work. Surveys for beta radiation hazard of the pump impeller and internal

components were not made prior to allowing work to commence on them.

After the work was completed contact beta radiation dose rates were

determined to be as high as 1,100 Rads per hour. While performing the

work without accurate knowledge of the beta radiation dose rate did not

lead to an overexposure, it may have resulted in unnecessary exposure"

(NRC inspections 50-277/91-28 and 50-278/91-28.)

September 24, 1991 - PECO determined that there was "induced

fuel failure" at Unit 3. "The licensee visually inspected the six bundles and

identified that one of the bundles had experienced failure caused by a

malfunctioning defect, while the other five bundles had experienced debris

induced failure. The debris appeared to be small metal chips" (NRC

inspections 50-277/91-33 and 50-278/91-33.)

September 27 through November 4, 1991 - During this inspection

period the NRC found "certain" of PECO's activities to be in "violation." A

Notice of Violation was issued. "Inadequate initial and independent

verification of a valve position resulted in an emergency core cooling

pump being inoperable for about seven days.The consistency and quality

of worker and independent verification of safety-related operations,

maintenance and test activities is a recurring weakness" (NRC inspections

50-277/91-30 and 50-278/91-30.)

October, 1991 - Employees using the wrong shutdown manual

caused an overheating of the plant's boron injection water. Larry Doerflein

of the NRC commented: "By and large, there has been little overall

progress. We're still seeing the same problems we saw a year ago" ("Atoms

& Waste," October, 1991.)

October 2, 1991 - The NRC issued a violation "associated with

inadequate radiation surveys during work on highly radioactive

components" (NRC IR50-277/92-80 50-278/92-80.)

October 16, 1991 - Unit 2 was shut down at 73% power due to the

inoperability of the high pressure coolant injection. A steam isolation

valve packing leak had been detected.(NRC inspections 50-277/91-30 and

50-278/91-30.) (For related incidents see: February 24, 1991; May 18

and 21, 1991; July 15-19, 1991; and, August 25, 1991.)

October 21-25, 1991 - "One non-cited violation was noted involving

radioactive material receipt practices (NRC inspections 50-277/91-32 and

50-278/91-32.)

October 22, 1991 - A fire in the Unit 3 condenser bay occurred

from 10:23 p.m. to 10:37 p.m. (NRC inspections 50-277/91-30 and 50-

278/91-30.)

October 25, 1991 - "The main control ventilation system

automatically isolated and transferred the emergency ventilation mode..."

(This type of actuation also occurred on September 17, 18 and 24, 1991.)

(NRC inspections 50-277/91-30 and 50-278/91-30.)

October 26, 1991 - An unusual event was declared when a

"potentially contaminated individual" was transported offsite.(NRC

inspections 50-277/91-30 and 50-278/91-30.) (See December 8, 1991 for

related incident.)

October 27, 1991 - Nuclear Maintenance Division "found the fuel

bundle at spent fuel pool location Z-31 to be oriented improperly" (50-

277/91-30 and 50-278/91-30.)

October 28, 1991 - "Smoke was detected coming from the Unit 2 "B"

Low Pressure Coolant Injection (LPCI) swing bus. Further examination

revealed that the power monitoring relay for the bus had burned up" (NRC

inspections 50-277/91-30 and 50-278/91-30.)

October 28, 1991 - The "B" auxiliary boiler was contaminated with

radioactive iodine-131. The boiler was isolated and radioactive liquid was

drained to the radwaste system. (See December 23, 1991 and February

24, 1992 for related incidents.)

November 4, 1991 - "The Unit 2 'B' reactor protection system (RPS)

motor generator (MG) set unexpectedly tripped" (NRC inspections 50-

277/91-30 and 50-278/91-30.)

November 8, 1991 - PECO "determined that the automatic

depressurization system (ADS) had been inoperable from shortly after the

plant startup in December 1989 to shutdown for the refueling outage on

September 14, 1991. The licensee concluded that the environmental

qualification (EQ) of the solenoid operated valves (SOV), electrical cables

and splices, to the five ADS safety related valves (SRV) had expired shortly

after startup. The thermal insulation over all 11 SRVs, including the 5

SRVs dedicated to ADS, had been installed backwards during the last

refueling outage" (NRC inspections 50-277/91-33 and 50-278/91-33.)

December 1, 1991 -In PECO's "Report to Shareholders, Third

Quarter, 1991,"it was revealed that a management audit was conducted

from July, 1989 to May, 1990. The audit was completed by Ernst & Young

and released in August, 1991. Philadelphia Electric admitted that the

audit "details a significant number of opportunities for the Company to

improve in almost every aspect of operations, and we have submitted a

detailed implementation plan to the PUC addressing each of the

recommendations for improvement."

December 5, 1991 - Unit 2 was forced to shutdown due to excessive

leakage past the residual heat removal system injection check valve. (NRC

inspections 50-277/91-33 and 50-278/91-33.)

December 5, 1991 - A reactor core isolation occurred at Unit 2.

(NRC inspections 50-277/91-33 and 50-278/91-33.)

December 8, 1991 - An unusual event was declared when a

potentially contaminated individual was transported off site. (NRC

inspections 50-277/91-33 and 50-278/91-33.) (See October 26, 1991 for

related incident.)

December 16, 1991 - At Unit 3, "an unexpected primary

containment isolation occurred..." during instrument line-up (NRC

inspections 50-277/91-43 and 50-278/91-34.)(See March 10, 1992 for

related incident.)

December 18, 1991 - A shutdown cooling isolation occurred at Unit

3 "when a PCIS logic fuse blew" (NRC inspections 50-277/91-43 and 50-

278/91-34.) (See January 4, 1992 for related incident.)

December 23, 1991 - Low-level iodine-131 contamination was

reported at the "B" and "C" auxiliary boilers. (See October 28, 1991 and

February 24, 1992 for related incidents.)

December 24, 1991 - In a letter to Mr. D.M.Smith, Senior Vice

President-Nuclear, the NRC identified two problems at Peach Bottom. "The

first problem concerns the degradation, and potential extended

inoperability, of the Unit 3 automatic depressurization system due to the

incorrect installation of the valve thermal insulation. In addition, your

immediate corrective actions following discovery of this problem were not

completely effective. A similar problem on one Unit 2 valve was not

identified and corrected until raised by the inspector. Based on our review

of the issues, two apparent violations of NRC requirements were identified

and are being considered for escalated enforcement action..." (Charles W.

Hehl, Director, Division of Reactor Projects.)

January 4, 1992 - Due to valve fuse failure, PECO "determined

that containment integrity could not be assured for the reactor core

isolation cooling suppression pool suction line" (NRC inspections 50-

277/91-34 and 50-278/91-34.) (See December 18, 1991 for related

incident.)

January 17, 1992 - High oxygen concentration levels were

recorded in the Unit 3 control room.

February 24, 1992 - The NRC reviewed PECO's efforts to desludge

the flood drain waste storage tank and found several problems: "...The

radiation protection technician who wrote the permit was unaware that

personnel would be walking in radioactive sludge measuring up to 350

millirem per hour (mr/hr) on contact...The radiation protection

supervisor who signed the RWP was not aware that workers would be

working in sludge...the planning process did not evaluate the collective

radiation exposure that would result from desludging all tanks over the

life of the PM process... The work activity was not reviewed by the ALARA

group, which precluded in-depth evaluation of all exposure reduction

methods, including the use of state-of-the-art cleaning techniques or

design changes to tanks to provide for ease of future cleaning that would

reduce aggregate exposure...The filter clogged and resulted in additional

personnel exposure...the licensee contacted no other stations to identify

state-of-the-art methods to perform tank desludging" (NRC IR 50-277/92-

80 and 50-278/92-80.)

February 24, 1992 - Low-levels of iodine-131 contamination in the

"A" auxiliary boiler were reported. (See October 28 and December 23,

1991 for related events.)

February 24 through March 13, 1992 - The NRC's Integrated

Performance Assessment Team (IPAT) issued its findings and "concluded

that several weaknesses merit near-term corrective actions to reduce the

potential for future safety problems...the team observed weaknesses in

licensee evaluation of degraded or inoperable control room

instrumentation and permanently installed plant instrumentation.

Weaknesses were also identified in the lack of interim corrective actions for

self-assessment findings and in the control of documents related to

modifications and temporary plant and procedure changes" (NRC Region I

IPAT IR 50-277/92-80 and 50-278/92-80.)

February 25, 1992 - Philadelphia Electric agreed to pay

$285,000 in fines for the improper insulation of safety system

relief valves at Unit 3. Company spokesman Neil McDermott admitted

there is "absolutely no question and we readily admit that the insulation

was improperly installed" (Patriot News, February 25, 1992.)

March 6, 1992 - The NRC observed: "Several weaknesses were

noted in the training program during the conduct of the examinations.

Differences between Peach Bottom and Limerick had a negative impact on

some LSRO lesson plans in that the lesson plans did not track actual plant

practice. LSRO responsibilities were not well defined at Limerick and differ

from those at Peach Bottom. Training was not always given as described in

the task to training matrix or the qualification manual. In general, the

candidates' knowledge of the site and plant at which they were not

normally stationed was weak." (Lee H. Bettenhausen, Chief, Operations

Branch, Division of Reactor Safety.)

March 10, 1992 - PECO "concluded" that Units 2 & 3 had

deficiencies in their primary containment isolation systems.(NRC

inspections 50-277/92-07 and 50-278/92-07.) (See December 16, 1991

for related incident.)

March 10, 1992 - The NRC's Integrated Performance Assessment

Team (IPAT) observed, "an operator exit the fourth floor administration

building radiological control point...without properly surveying personal

articles being removed from the radiological control area" (NRC Region I

IPAT 50-277/92-80 and 50-278/92-80.)

March 13, 1992 - Philadelphia Electric "discovered" Unit 2 residual

heat removal equipment valves were not installed."With the check valves

on the discharge of the sump pumps for the 'B' and 'D' RHR rooms not

installed, this design basis can not be met. Specifically, during a loss of

coolant accident, concurrent with a loss of off-site power, the reactor

building sump pumps would not be available due to the loss of off-site

power" (NRC inspections 50-277/92-07 and 50-278/92-07.)

March 16, 1992 - Due to a turbine exhaust drain line valve failure,

the Unit 2 high pressure coolant injection system was rendered

inoperable.(NRC inspections 50-277/92-07 and 50-278/92-07.) (See

March 23, 1992 for related incident.)

March 23, 1992 - PECO "declared the HPCI system inoperable

when the turbine overspeed trip device did not reset during testing" (NRC

inspections 50-277/92-07 and 50-278/92-07.) (See March 16, 1992 for

related incident.)

March 26, 1992 - PECO "declared all Unit 2 reactor water level

instrumentation associated with the 2B reactor water level reference leg

condensing chamber inoperable" (NRC IR 50-277/92-13 and 50-278/92-

13.) (See September 11, 1990, March 27, 1992 and July 26, 1992 for

related incidents.)

March 27, 1992 - Unit 2 was shutdown due to inoperable reactor

level instrumentation. (See September 11, 1990, March 26, 1992 and

July 26, 1992 for related incidents.)

April 2, 1992 - A settlement was announced on the two lawsuits

brought against PECO by Peach Bottom's co-owners: Public Service Electric

and Gas Company, Delmarva Power and Light Company and Atlantic City

Electric Company. The suits were related to the NRC shutdown of Peach

Bottom on March 31, 1987."As part of the settlement, Philadelphia

Electric will pay $130,985,000 on October 1, 1992 to resolve all

pending litigation." (Joseph Paquette, April 8, 1982.) (See July 27,

1988 for background material.)

April 7, 1992 - PECO began a planned shutdown for Unit 2 from

about 100% power. "The shutdown was required because a one inch vent

line failed at a welded connection on the condensate supply herder to the

offgas recombiner condenser...A reactor scram and primary containment

isolation system (PCIS) group II and III occurred" (NRC IR 50-277/92-09

and 50-278/92-09.)

April 17, 1992 - The NRC issued a Notice of Violation for the

following infractions: "Contrary to the above requirements, the ODCM

[Offsite Dose Calculation Manual] specified composite water sampler at the

intake had been inoperable during the period August 30, 1991 to March

19, 1992, and the specified composite water sampler at the discharge had

been inoperable since August 8, 1991 and remains inoperable at the time

this inspection [was] conducted March 23-27, 1992. The licensee's efforts

to complete corrective action prior to the next sampling period were

ineffective" (NRC inspections 50-277/92-08 and 50-278/92-08.)

April 29, 1992 - A Health Physics technician was contaminated

in the de-watering facility when "contamination controls were

compromised. According to the licensee's investigation, a defective latch

and hinge on the fill-head access door allowed contamination to escape

from the liner to the room during processing. Contamination levels on

near-by radwaste equipment were as high as 200 mrad/hour. The

general area surfaces in the truck bay were contaminated up to 30,000

dpm/100cm (2)" (NRC IR 50-277/92-12 and 50-278/92-12.)

May 4, 1992 - Philadelphia Electric "initiated a planned shutdown

[at Unit 3] in order to repair a large steam leak through a manway on the

'F' moisture separator tank" (NRC inspections 50-277/92-11 and 50-

278/92-11.)

May 12, 1992 - Unit 3 recirculation pump trip occurred at 80%

power.(See June 27, July 23, July 26 and July 27, 1992 for related

incidents.)

May 15, 1992 - PECO initiated a shutdown of Unit 2 "due to

inoperability of the high pressure coolant injection and the reactor core

isolation cooling systems" (NRC inspections 50-277/92-11 and 50-278/92-

11.) (See June 25, 1992 for related incident.)

May 20, 1992 - Unit 2 experienced a reactor scram and turbine

trip due to a malfunctioning combined intermediate valve.

May 22, 1992 - The motor for the Unit 3 residual heat removal

pump failed and was declared inoperable.

June 1, 1992 - "Common stock earnings for the first quarter of

1992 were $0.33 per share, $0.25 lower than the $0.58 per share

earnings for the corresponding period last year. The reduction in earnings

was primarily the result of the previously reported settlement of litigation

by the co-owners of Peach Bottom Atomic Power Station which reduced

first quarter earnings by approximately $0.27 per share" (J.F. Paquette,

Jr., Chairman of the Board and Chief Executive Officer, Report to

Shareholders First Quarter, 1992).

June 25, 1992 - The Unit 3 high pressure coolant injection system

was declared inoperable "due to excessive water buildup in the turbine

casing" (NRC IR 50-277/92-13 and 50-278/92-13.) (See May 15, 1992 for

a related incident.)

June 27, 1992 - The 'A' recirculation pump tripped at Unit 2.(See

May 12, July 23, July 26 and 27, 1992 for related incidents.)

July 4, 1992 - An Alert was declared at Peach Bottom due an

explosion at the #1 transformer station. Units 2 and 3 were operating at

at, or around, 95 % power. As a result of the explosion, Unit 3 scrammed

and there were several emergency safeguard actuations.(See May 2, 1991

for a related incident.)

July 14, 1992 - "Unit 3 was manually scrammed from 63% power

due to a decreasing main condenser vacuum" (NRC IR50-277/92-13 and

50-278/92-13.)

July 17, 1992 - Unit 2 experienced a turbine trip and reactor

scram at 95% power during a severe lightning storm.

July 23, 1992 - The Unit 3 recirculation pump tripped at 95%

power.(See May 12, June 27, July 26 and July 27, 1992 for related

incidents.)

July 25, 1992 - "Unit 2 was shutdown due to a safety relief valve

bellows rupture alarm" (NRC IR 50-277/92-13 and 50-278/92-13.)

July 26, 1992 - The 'A' recirculation pump tripped at Unit 2. (See

May 12, June 27, July 23 and July 27, 1992 for related incidents.)

July 26, 1992 - A safety device used at Peach Bottom and 35 other

American nuclear reactors may be defective according to the NRC.

"Engineers are concerned that in a serious accident involving the rapid

loss of coolant and pressure from the reactor, the device would give a false

reading, indicating the reactor core was still covered with water when it

actually was not and therefore in danger of melting down" ( Sunday

Patriot News, July 26, 1992 A3.) (See September 11, 1990 and March 26

and 27, 1992 for related incidents.)

Peach Bottom has had a history of problems in this area.

" In August 1990, the licensee identified that the Unit 2 level

instrumentation served by the 2B condensing chamber and reference leg

was indicating values about 11 inches higher than similar instruments

served by the 2A condensing chamber...They [PECO] concluded that the

actuation set points for several safety systems would be exceeded during

transients or accidents, declared the instruments inoperable and

completed a plant shutdown. Following the 1990 event, the licensee

revised the channel check procedures to provide better monitoring and

evaluation of the instruments...A second level offset event, again

Continued on the next page...

involving the Unit 2B condensing chamber, occurred in March 1992. The

improved surveillance procedures helped the licensee identify the offset

before it had exceeded 3 inches. In response, the licensee established a 4

1/2 inch offset operability limit, and closely monitored the

instrumentation..." (NRC IR 50-277/92-16 and 50-278/92-16.) ( For

related incidents see September 11, 1990 and March 26-27, 1992.)

July 27, 1992 - The 'A' recirculation pump tripped at Unit 2.

(See May 12, June 27, July 23 and July 26, 1992 for related

incidents.)

July 27, 1992 - Peach Bottom and 86 other suspected nuclear

reactors "depend on a defective and dangerous fire-barrier system

to protect electrical cables used for a safe shutdown during a

fire/accident." (Nuclear Information and Resource Service (NIRS), July

27, 1992.) The company who produces the Thermo-Lag 330 system is

Thermal Science, Inc. (TSI), St. Louis, Missouri. Among the problems with

Thermo-Lag are: combustibility, toxicity, seismic qualification,

vulnerability to water, incomplete installation and ampacity calculation

errors.

In an IR issued on September 10, 1992, PECO requested a temporary

waiver of technical specification compliance for certain fire barriers. The

NRC observed: "...the licensee could not post the required fire watch for

residual heat removal system cables running through the Unit 3 offgas

pipe tunnel because it is a high radiation area".

(NRC IR 5 277/92\16 and 50-278/92-16.)

August 6, 1992 - The NRC issued a violation "for operation of the

reactor cleanup system in a mode not established in approved operating

procedures, is of concern because it represents a weakness in your control

of operating activities" (NRC IR 50-277/92-13 and 50-278/92-13.)

August 10, 1992 - PECO entered a seven day maintenance outage on

the E-4 emergency diesel generator.

August 17, 1992 - A generator lock-out and reactor scram occurred at

Unit 2 due to improper blocking. PECO "determined that the generator

lock-out occurred because the permit being applied in the South Substation

was incorrect" (NRC IR 50-277/92-16 and 50-278/92-16.)

August 20, 1992 - The Unit 3 Emergency Core Coolant System power

supply failed. The root cause was a failed topaz inverter.

September 14, 1992 - A licensed operator tested positive for

marijuana use.

October 6, 1992 - During an NRC inspection relating to plant

security, one unresolved Fitness-for-Duty(FFD) item was identified. The

NRC also cautioned that "... additional attention is warranted on the

effectiveness of routine security patrols since we identified certain

deficiencies during this inspection that should have been identified by

your officers on patrol" (NRC IR 50-277/92-20 and 50-278/92-20.)

October 15, 1992 - Unit 3 scrammed and the high pressure coolant

injection (HPCI) system initiated: "... Unit 3 experienced a primary

containment isolation system (PCIS) group I isolation on main steam line

(MSL) low pressure. This resulted in closure of the MSIVs and a reactor

scram. During the post-scram pressure and level transient, vessel water

decreased to the ECCS Lo Level initiation setpoint. The high pressure

coolant injection (HPCI) and reactor core isolation cooling (RCIC) systems

initiated and injected into the reactor vessel. The alternate rod insertion

and reactor recirculation point trip logic also actuated. Three main steam

safety relief valves (SRV) opened automatically for a short period to

control pressure, and later re-closed. The licensee declared an unusual

event (UE) at about 9:25 p.m. due to the initiation and ejection of an

ECCS system in response to a valid signal...At about 11;16 p.m., while

proceeding with the plant cooldown, reactor vessel level increased above

the normal operating band and caused a HPCI and RCIC high reactor

vessel water level turbine trip. Due to the temporary loss of HPCI as a

means of pressure control, reactor pressure increased to the high pressure

scram setpoint. the operators manually operated an SRV to reduce

pressure, and restarted HPCI and RCIC. the licensee also reported this

second scram signal to the NRC via the ENS. All systems responded as

expected following the PCIS group I isolation and reactor scram, and the

subsequent high reactor pressure scram" (NRC IR 50-277/92-27 and 50-

278/92-27.)

PECO management decided to shut the plant for five days.

After reviewing the events the NRC issued a Notice of Violation and

criticized, "The control room staff did not effectively monitor developing

reactor coolant stratification following the Unit 3 automatic scram, and

certain Technical Specification reactor pressure/temperature limits were

exceeded. Adequate controls were not in place to ensure that the transient

was appropriately evaluated before plant restart. Also, operators did not

record required pressure data used to evaluate compliance with

pressure/temperature limits following a Unit 2 shut-down." (E.

Wenzinger, Chief, Projects Branch 2, Division of Reactor Projects,

November 16, 1992.)

October 16, 1992 - The NRC found one potential problem with senior

reactor operators (SRO) examinations:"Since SRO Upgrades are currently

licensed individuals at your facility, we are concerned that your training

program may not be emphasizing a high level of performance among

reactor operators in referring to and using procedures" (NRC IR 50-

277/92-18 and 50-278/92-18.)

October  15,  1992  -  Unit-3  scrammed  and  recirculation  pumps  shutdown,

“there was a  significant  cool down in the bottom head as a  result of the loss of

forced  circulation”  (IR  50-277/94-04  and  50-278/94-04.)

October  16,  1992 -  The  NRC  identified  programmatic  weaknesses  related

to  the  System  Manager  program.  (NRC  IR  50-277/92-26  and  50-278/92-26.)

November  16,  1992 -  The  NRC  noted:  “An  industrial  safety  concern,

which  involved the  potential  for  loss  of  power  in the  drywell...had  not  yet  been

resolved  and  warrants  your  attention”  (NRC  IR  50-277/92-30  and  50-278/92-

30.)  (See  December  12,  1995  for  a  related  incident.)

December  2  and  11,  1992 -  Failures  of  the  containment,  atmospheric,

dilution (CAD)  system  gas  analyzer  occurred  at  Unit-2.  On  both  occasions  PECO

personnel  did  not  “understand”  or  “recognize” the  problem  with the  CAD. (NRC

IR  50-277/92-29  and  50-278/92-29.)

December  4,  1992 -  Several  weaknesses  were  reported  during the  the

Initial  SALP  of  Licensee  Performance  “including  numerous  component  failures,

lapses  in  the  operating  procedure  and  deficiencies  in  engineering  and  technical

support”  (York  Daily  Record,  January  9,  1993.)  “Among  the  areas  identified  for

improvement  were  plant  performance  monitoring  and  engineering  and

technical  support”  (PECO, Report to the Shar eholde r s, March  1,  1993.)

December  7,  1992 -  During  Unit-2  start-up,  the  ‘2B’  Recirculation  Pump

failed.  (NRC  IR  50-277/92-32  and  50-278/92-32.)  (See  March  2,  1993  for  a

related  incident.)

December  17,  1992 -  Turbine  control  oscillations  occurred  while  Unit-2

was  operating  at  89.5%  power.  The  plant  was  “stabilized”  at  76.5%  power. (NRC

IR  50-277/92-32  and  50-278/92-32.)

December  19,  1992 - An Unusual Event was declared  “due to  a loss  of

emergency  communications  capabilities.  Both  units  were  operating  at  20%

power”  (NRC  IR  50-277/92-32  and  50-278/92-32.)

January  1,  1993  -  The  Unit-2  high  pressure  coolant  injection  system  was

declared  inoperable.  (NRC  IR  50-277/92-32  and  50-278/92-32.)  (See  January

25  and  31,  March  1  and  August  9,  1993,  for  related  incidents.)-  January  21,  1993 - A  Notice  of Violation (NOV)  was  issued  relating to the

NRC’s Motor-Operated Valve (MOV) Inspection  on  October  19-23  and  November

3,  1992.  PECO  “1)  did  not  document  nonconforming  positions,  2)  did  not

properly  disposition  existing  nonconforming  conditions,  and  3)  did  not take

timely  corrective  actions  to  evaluate  and  resolve  nonconforming  conditions  in

MOVs...”  (NRC  IR  50-277/92-82;  50-278/92-82.)  (See  August  8-16,  1998,  for  a

related  incident.)

- January  25,  1993  -  During  surveillance  testing,  the  Unit-3  high

pressure  coolant  injection  system  was  declared  inoperable.  (NRC  IR  50-277/93-

- 01  and  50-278/93-01.)  (See  January  1  and  31,  March  1  and  August  9,  1993,  for

related  incidents.)

January  31,  1993  -  The  Unit-2  high  pressure  coolant  injection  system

was  declared  inoperable.  (NRC  IR  50-277/93-01  and  50-278/93-01.)  (See

January  1  and  25,   March  1,  and  August  9,  1993,  for  related  incidents.)

March  2,  1993 -  Unit-2  scrammed  while  operating  at  70%  reactor  power.

(NRC  IR  50-277/93-03  and  50-278/93-03.)

March  2,  1993 -  The  Unit-2  ‘2A’  reactor  recirculation  pump  and  ‘2A’

condensate  pump tripped  while the  Unit  was  operating  at  100%  power” (NRC IR

50-277/93-03  and  50-278/93-03.)  (See  December  7,  1992  for  a  related

i n c i d e n t . )

March  3,  1993 -  The  Unit-2  high  pressure  coolant  injection  system  was

declared  inoperable.  (NRC  IR  50-277/93-03  and  50-278/93-01.)  (See  January

1,  25  and  31  and  August  9,  1993  for  related  incidents.)

March  7,  1993 - [R]eactor  scram,  due to  a  low  reactor  vessel  level.

Reactor  feed  pump  trip  while  lowering  reactor  power  to  with  in  bypass  valve

capacity,  to  allow  work  on  turbine  valves”   (IR  50-277/94-04  and  50-278/94-

0 4 . )

March  10,  1993  -  During  a  radiological  safety  inspection  (February  8-9,

1993  and  March  1-2,  1993),  relating  to  a  “breakdown  of  personnel  access

controls  associated with the Transversing In-core Probe (TIP), the NRC found:

“...control  of  personnel  during  such  operations  is  considered  very  important  as

the TIPs  represent  one  of the  higher  radiation  sources that  personnel  have  a

potential  for  encountering”  (NRC  IR  50-277/93-02;  50-278/93-02.)  (For  related

incidents  see  June  22  and  25,    September  24,  October  4,  and  November  11,

1993;  June  19  and  November  29,  1994  and  August  24,  1995.)

March  23,  1993 -  High  oxygen  concentration  was  found  in  Unit-  2

containment  during  power  operation.  (NRC  IR  50-277/93-03  and  50-278/93-

03.)  (See  January  17,  1992  for  a  related  incident.)-  April  24,  1993  -  Unit-2  was  manually  scrammed  “following  declaration

of  all  reactor  vessel  level  instrumentation  served  by  the  ‘2B’  condensing

chamber  inoperable”   (NRC  IR  50-277/93-06  and  50-278/93-06.)  (See  related

incident  on  March  27  and  July  26,  1992  and  September  22,  1993.)

April 30,  1993 - A Notice of Violation was issued following  an  an NRC

inspection  of  the  electrical  distribution  system.  Other  design  and  operational

weaknesses  were  identified  relating to the  emergency  diesel  generator. (NRC IR

50-277/93-80  and  50-278/93-80.)  (See  July  17,  1995  for  a  related

d e v e l o pme n t . )

May  26,  1993 -  Three  individuals  were  found  to  be  “inattentive”  or

“sleeping.” (C. Anderson,  NRC  Region I.)

June  22,  1993 -  “Controls  over  a  special  high  radiation  area  entry  were

not  fully  effective  in that  a  higher than  expected  dose  rate  was  identified  upon

the  entry”  (IR  50-277/94-04  and  50-278/94-04.)  (See  March  10,  June  25,

September  24  and  October  4  and  November  11,  1993  and  January  19  and

November  29,  1994.)

June  24,  1993 - PECO  discovered  a  “mispositioned”  control  rod  at Unit-2.

The  reactor  was  operating  at  60%  power. (NRC IR  50-277/93-15  and  50-

278/93-15.)  (For  related  events  see  February  22,  1994,  April  21,  1995  and

February  15,  1997.)

June  25,  1993  “[U]unlock[ed]  high  radiation  area  door”  (IR  50-277/94-

04  and  50-278/94-04.)  (See  March  10,  June  22,  July  22,  September  24,

October  4  and  November  11,1993  and  January  19  and  November  29,  1994.)

July  4,  1993 -  Unit  3  was  shutdown.  “An  unplanned  Unit  3  mid-cycle

outage  began  on  July  6,  1993, to  replace to  known  leaking  fuel  bundles.”   A  fuel

leak  was  detected  in  May  1992.   (NRC  IR  50-277/93-15  and  50-278/93-15.)

- July  30,  1993 -  Unit-3  was  manually  scrammed  “after  a  loss  of

condenser  vacuum”  (NRC  IR  50-277/93-15  and  50-278/93-15.)

August  9,  1993 -  The  Unit-3  high  pressure  injection  system  was  rendered

inoperable  (NRC  IR  50-277/93-17  and  50-278/93-17.)  (For  related  incidents

see,  January  1,  25  and  31  and  March  1,  1993.)

August  11,  1993  -  Unit-2  was  manually  scrammed.  (NRC  IR  50-277/93-

17  and  50-278/93-17.)

August  14,  1993 -  Unit-3  was  shut  down  after three  of four  residual  heat

pumps  were  deemed  inoperable.  The  plant  was  operating  at  100%  power. (NRC

IR  50-277/93-17  and  50-278/93-17.)-  September  14,  1993 - The  reactor feed  pump tripped  due to  “flow

oscillations”  at  Unit-3.

September  16,  1993 -  An  inspection  of  Peach  Bottom’s  Emergency

preparedness  program  on  June  28-30,  1993  found:  “Significant  areas  for

potential  improvement  included  wind  direction  information  use  by  emergency

response  groups,  event  announcements  in  the  Emergency  Operations  Facility  by

the ERM [Emergency Response Manager],  and ERM  recognition  of the best

indication  of  main  stack  radiation”  (NRC  IR  50-277/93-10;  50-278/93-10.)

September  22,  1993 - The NRC  “noted that weaknesses in isolation  of the

reactor  vessel  water  level  instrumentation  during  installation  of  the  [water  level

backfill] modification  resulted  in the  generation  of  a false  low  signal.  This  low

label  signal  caused  the  ECCS  initiation  signals  and  entry  into  a  technical

specification  required  shutdown  condition  at  Unit  3”   (For  related  incidents  see,

March  27  and  July  26,  1992  and  April  24,  1993.)  Also  the  NRC  completed  their

investigation  into  the  recirculation  pump  trip  on  July  27,  1992.  (NRC  IR  50-

277/93- 17  and  50-278/93- 17. )

September  24,  1993 -  “Workers  in  Unit-3  were  unaware  of  higher  than

expected  radiation  levels”  (IR  50-277/94-04  and  50-278/94-04.)  (See  March

10,  June  22  and  25,   October  4  and  November  11,  1993  and  January  19  and

November  29,  1994.)

September  24,  1993 -  “During  core  off  load  a fuel  bundle  became  stuck

partially  inserted  in  its  storage  rack  in the Unit  3 fuel  pool...” (NRC IR  50-

277/93-24  and  50-278/93-24.)  (See  February  21-22,  1993  for  related  events.)

October  4,  1993 - An  NRC  inspection (August  2-6,  1993)  found:  “The

lack  of  comprehensive  corrective  actions  for  some  radiological  discrepancies

developed  under the  ROR [Radiological Occurrence  Reporting]   process was

considered  a  significant  radiological  controls  program  weakness.   A  previous

audit  of  the  radiological  controls  program  by  the  NQA  [Nuclear  Quality

Assurance]  identified  a  significant  breakdown  concerning  radiological  controls

oversight. In  particular,  a  weakness  was  noted  in  the  area  of  radiation  worker

attention  to  detail  and  adherence  to  instructions  provided  by  radiological

controls  staff”  (NRC  IR  50-277/93-19;  50-278/93-19.)  (See  March  10,  June  22

and  25,   October  4,  September  24  and  November  11,  1993  and  January  19  and

November  29,  1994.)

- October  6,  1993 -  “[C]ontrol  switch  for  control  room  emergency

ventilation  left  in  the  off  position  following  restoration” (IR  50-277/94-04  and

5 0 - 2 7 8 / 9 4 - 0 4 . )-  November  11,  1993  “Unlocked  high  radiation  door”  (IR  50-277/94-04

and  50-278/94-04.)  (See  March  10,  June  22  and  25,  September  24  and  October

4,  1993  and  January  19  and  November  29,  1994.)

November  15,  1993 -  “5th  point  heater  valve  out  of  position  following

Unit-3  start-up,  leading  to  a  steam  leak  to  the  turbine  building”  (IR  50-277/94-

04  and  50-278/94-04.)

November 22,  1993 - A Notice  of Violation was issued for  “a poor  safety

review  of  a temporary  change to  a  reactor  core  isolation  cooling testing

procedure  led  to  the  inadvertent  release  of  radioactive  contamination  within  the

Unit  3  reactor  building.  While  this  resulted  in  a  minor  clothing  contamination,

our  review  indicated  poor  management  review  and  control  of  activities  related

to  the  specific  testing”  (NRC  IR  50-277/93-24  and  50-278/93-24.)

December  18,  1993  -  “Missed  continuous  fire  watch”  (50-277/94-04  and

50-278/94-04.)  (See  similar  incidents  on  August  4,  1994  and  January  11,  1998

and   related  data  on  Thermo-Lag,  September  29,  1994  and  October  1,  1996.)

January  1  ,  1994  -  Philadelphia  Electric  Company  changed  its  name  to

PECO  Energy  Company.

January  19,  1994  -  “During  the  inspection  [October,  4-8  and  November

8- 10,   1993] the  NRC  reviewed  the  circumstances  associated  with  three

examples  of  failure  by  three  different  individuals  to  adhere  to  procedural

requirements  concerning  entries  to  high  radiation  areas  in  two  cases,  and  a

respiratory  protection  required  area  in  the  third  case.”   A  Severity  Level III

violation  was  announced  by  the  NRC.

“Particularly  disturbing  to  the  NRC  is  the  fact  that  the  plant  equipment

operator,  on  October  27,  and  the  engineer  on  October  29,  willfully  violated  the

radiological  controls  in  that  they  understood  that  they  were  no  to  enter  the

areas,  yet  did  so  anyway  to  complete  certain  tasks  without  first  meeting  the

necessary  radiation  protection  requirements.  The  entry  by  the  engineer  on

October  29  was  more  significant  since  he  had  been  warned  by  health  physics

personnel  not to  enter the  area  pending  receipt  of  air  activity  results,  yet  did  so

anyway”   (Thomas  Martin,  NRC,  Regional  Administrator,  January  19,  1994.)

(See March  10,  June  22  and  24,  September  24  and  October  4,  1993  and

November   29,  1994  for  related  incidents.)

January  24,  1993 -  The  High-Pressure  Coolant Injection  system  was

declared  inoperable  in  Unit-3.

February  3,  1994 -  Unit-3  was  manually   scrammed  due  to  a  Generator

Field  Ground  alarm.  The  reactor  was  operating  at  100%  power.-  February  22,  1994 -  During  power  restoration  at  Unit-2,  a  control  rod

(38-15)  was  mispositioned  for  approximately  two  minutes.  (For  related  events

see  June  24,  1993,  April  21,  1995  and  February  15,  1997.)

February  23,  1994 - A  jet  pump  grappling  hook  was  dropped  into the

Unit-3  spent fuel pool.

March  3,  1994 -  Two four  hour  event  notification  reports  were filed  with

the  NRC  due to the  inoperability  of the  control  room  emergency  system  and

problems  associated  with  the  Unit-2  high  pressure  coolant  injection  system.  Both

reports  were  later  retracted.

March  9,  1994 - Increased  contamination  was  detected  in the  Unit-3  high

pressure  coolant  injection,  pump  room.  As  a  result,  seven  shoe  contamination

reports  were  filed.

March  31,  1994 -  A  high-pressure  coolant  injection  leak  was  identified.

-  Spring  1994 -  “The  Public  Utility  Commission (PUC)  recently  approved  a

settlement  with  PECO  Energy  Company  (PECO.)  PECO  will  give $217,000 to a

grant  program  for  low  income  consumers  and  pay  a  $24,000  fine  for  violating

PUC  regulations.  For  1991, the  PUC found  241  violations  of the  Commission’s

regulations. Many  had to  do  with  PECO’s  handling  of  billing  disputes  and  service

shut-offs”   (”Utility Consumer Line,” Bureau  of Public Liaison, PA PUC,

Spr ing/Summe r   1994. )

April  18,  1994  -  Further  weld  thinning  was  identified  in  the  Emergency

Service  Water  supply  .

April  27,  1994 -  Unit-s  experienced  a  reactor  vessel  water  transient.

“Pitting”  was  identified  in  this  area  in  November  1993.

May  14,  1994 -  Power  was  reduced  at  Unit-2  to  “approximately  77%  to

perform  a  rod  pattern  adjustment  and  to  repair  a  non-safety  main  steam

moisture  separator  drain  tank  (MSDT)  drain  valve.  During  the  power

restoration  on May  16,  the  2A  reactor  recirculation  pump (RRP)  speed  increased

unexpectedly,  (See  September  22,  1995)  causing  reactor  power  to  increase  above

the  average  power  range  monitor  flow  biased  high  power  scram  setpoint,

resulting  in  a  reactor  scram”  (IR  50-277/94-06  and  50-278/94-06.)  (See

October  24  and  November  10,  1994.)

May  26,  1994 - A  Severity  Level IV  violation  was  issued  after the  NRC

“identified  requirements  for  collecting  a  representative  sample  of  the  water  river

flowing  into the  site  were  not  being met” (Edward C. Wenzinger, Chief,  Projects

Branch  2,  Division  of  Reactor  Projects,  NRC.)-  June  16,  1994 -  The  NRC  reported the following  problems  during  Peach

Bottom’s  most  recent  Radiological  Emergency  Preparedness  Exercise:  “...14

Areas  Requiring  Corrective  Action (ARCA),  two  Planning Issues (PI),  and  eight

Areas  Recommended for Improvement (ARFI)  were  identified  in the

Commonwealth  of  Pennsylvania  and  the  State  of  Maryland  combined.”  (James

Joyner,  Chief,  Facilities  Radiological  Safety  and  Safeguards  Branch,  NRC.)

June  22,  1994 -  “PECO made four  10 CFR  50.72 four  hour  notification

reports to the  NRC  during the  period.  Subsequently,  PECO  retracted three  of the

event  reports”  (IR  50-277/94-06  and  50-278/94-06.)

- June  23,  1994 -  “The [NRC]  inspectors  continued to  review the

installation  of  the  new  control  room  radiation  monitoring  system...Specifically,

system  operating  procedures  were  not  in  place  when the  system  was  placed  in

service  and  considered  operable,  the  system  was  operated  in  an  unanalyzed mode

of  operation  because  of  unclear  documentation,  and  one  channel  of the  system

was  inadvertently  removed  from  service  due  to  the  use  of  an  improper  drawing

[A  Notice  of Violation  was  issued.]” Edward C. Wenzinger, Chief,  Projects Branch

2, Division  of  Reactor Projects, NRC.)

June  30,  1994 -  “Two  small  surface  cracks  were  found  last  September  in

welds on the  core  shroud of Peach Bottom Unit 3 near Delta., Pa.,  said Bill Jones,

a  spokesman for  PECO Energy  Co., the  plant’s  operator...The  shrouds  are  2-inch

thick  stainless  steel  cylinders  that  direct  the  flow  of  radioactive  water  around  the

fuel  core. A  nuclear  reaction  boils  water  into the  steam  used to  generate

electricity”  (The  Patriot  News,  July  1,  1994  A5.) (See  June  30,  1994  and  August

18,   1995. )

“Peach  Bottom  Unit  No.  3  was  initially  examined  during  its  refueling

outage  in  the  fall  of  1993.  Although  crack  indications  were  identified  at  two

locations, the  Company  presented  its findings to the  NRC  and  recommended

continued  operation  of Unit No.  3 for  a two-year  cycle. Unit No.  3 was  reexamined  during  its  refueling  outage  in the  fall  of  1995  and the  extent  of the

cracking  identified  was  determined  to  be  within  industry-established  guidelines.

The  Company  has  concluded,  and the  NRC  has  concurred, that there  is  a

substantial margin for  each  core  shroud  weld to  allow for  continued  operation  of

Unit  No.  3.  Peach  Bottom  Unit  No.  2  was  initially  examined  during  its  October

1994   refueling  outage  and  the  examination  revealed  a  minimal  number  of

flaws.  Unit  No.  2  was  re-examined  during  its  refueling  outage  in  September

1996.  Although  the  examination  revealed  additional  minor  flaw  indications,  the

Company  concluded,  and  the  NRC  concurred,  that  neither  repair  nor

modification to the  core  shroud  was  necessary.  The Company  is  also

participating  in  a  GE BWR  Owners  Group to  develop  long term  corrective

actions.”   (PECO  Energy  Company,  Form-10/K-A,  1999,  p.  1999)   A three-inch  crack  was  identified  in the  reactor  vessel  shroud  at

Brunswick-1    in the  summer  of   1993. Cracks  have  also  been found  in the  coreshrouds of Dresden-3  and Quad Cities-1. All of these  reactors  are GE Mark  1

designs.

July  18,  1994 - A  Severity  Level IV Violation  was  issued for failure to

implement   maintenance  procedures  on  the  Unit-2  high  pressure  coolant

injection  system. PECO  issued  an LER.

July  22,  1994  -  “PECO  identified  that  the  existing  instrument  reference

calibration  placards  were  incorrectly  installed  with  respect  to  the  bottom  of  the

torus  of  each  unit”  (IR  50-277/94-013  &  50-278/94-013.)  PECO  issued  an  LER.

July  27,  1994 - An NRC  inspection  “noted that   there  had  been  no  indepth training  provided to  some  of the [rad  waste]  shipping  engineers  since

1988...As  such,  the  training  provided  to  shipping  engineers  remains  a  program

weakness.  Licensee  management  informed  the  inspector  they  consider  their

current  shipping  engineer  training  program  to  be  adequate”   (IR  50-277/94-18

and  50-278/94-18.)

August  3,  1994  -   “...PECO  Energy  personnel  unknowingly  placed  the

emergency  cooling  water  system  in  a  configuration  that  prevented  safetyrelated  equipment  from  receiving  design  cooling  water  flow  rates...The  overall

safety  consequences  of  this  event  were  small...however,  this  condition

represented  a  significant  degradation  in  plant  safety...”  An  enforcement

conference  was  held  on  October  18,  1994. (Richard W. Cooper, II,  Director,

Division  of  Reactor  Projects,  NRC,   September  29,  1994.) (See  November  21,

1994  for  civil  penalty  and  violation.)

August  4,  1994 - PECO  personnel missed  a fire  watch. (See  December  18,

1993  and  January  11,  1998  for  related  incidents,  and  August  10  and  September

29,  1994  for  more  data.)

August  10,  1994 -  A  “minor”  fire  was  extinguished  on  the  Unit-2  reactor

building  roof.  During  this  episode,  the  Unit-2  secondary  containment  was

b r e a c h e d .

August  11,  1994  -  The  high-pressure,  coolant-injection  system  was

inoperable  during  maintenance  activities.  (See  September  24,  1994  for  related

i n c i d e n t . )

August  17,  1994 -   “...procedures  were  not  implemented  for  the  operation

of  the  reactor  building  [Unit-3]  ventilation  and  standby  gas  treatment  system”

(PECO  Energy,  Gerald  R.  Rainey, Vice  President,  Peach  Bottom Atomic  Power

Station,  October  19,  1994.)  A  Severity  Level  IV  Violation  was  issued. - August  18,  1994 - An NOV was issued  relating to  vision  problems  of  a

- LRO.

August  26,  1994 - A  NOV  was  issued  relating to Motor  Operated Valve

T e s t i n g

September  7,  1994 -  A  high-pressure,  service  water  pump  failed  at  Unit-

3 .

September  8,  1994 -  “Standard  and Poor’s Corporation (S&P)  has  revised

its  rating  outlook  on  the  company  from  ‘negative”  to  stable’” (J.F.  Paquette,  Jr.,

Chairman  of  the  Board  and  Chief  Executive  Officer.)

September  20,  1994 -  During  the  refueling  outage,  air  bubbles  were

found  leaking  into  the  reactor  cavity.

September 21,  1994 - PECO notified the NRC of a loss of  shutdown cooling

at  Unit-2  due  to  a  preventive  maintenance  operation.

- September  23,  1994 - A  broken fuel  rod  was  discovered.

September  24,  1994 -  A  high-  pressure,  coolant-injection  steam  supply

leak  was  discovered  at  Unit  3.  (See  August  11,  1994  for  related  incident.)

September  29,  1994 -  “Thermal  Science Inc.  and  its  president,  Rubin

Feldman,  were  indicted  September  29  by  a  federal  grand  jury  on  seven  criminal

charges,  including  willful  violations  of  the  Atomic  Energy  Act,  a  decade-long

conspiracy  to  defraud  the  US  government,  false  statements,  and  more.  The

charges  are  the  culmination  of  a  nearly  two-year  grand  jury  investigation  of  the

company,  which  manufactures  Thermo-Lag,  the  ineffective  fire  barrier  used  in

more  than  70  nuclear  reactors  [including  Peach  Bottom.]”  (The  Nuclear

Mo n i t o r , October  17,  1994.)  (See  December  18,  1993  and  October  1,  1996.)

October  10,  1994 -  The  NRC  reported  “four  individuals  entered the  Unit  2

offgas  pipe tunnel  high  radiation  area (HRA),  which  was  visibly  posted  as  a HRA,

and  the  individuals  were  not  provided  with  the  required  radiation  monitoring

device,  nor  was  positive  control  provided  by  an  individual  qualified  in  radiation

protection  procedures,  nor  did the  individuals  adhere to  posted  instructions

regarding  entry  requirements,  a  requirement  of  the  Radiation  Work  Permit

under  which  the  entry  was  made”  (IR  50-277/95-05  and  50-278/95-05  and

Notice  of  Violation.)  (See  October  31,  1994,  November  29,  1994  and  March  14,

1995  for  related  incidents  and  Notice  of  Violation.)-  October  16 -17,  1994   The  Unit-2  reactor  pressure  vessel (RPV)  exceeded

212  degrees  F.  “After  reviewing  operators’  involvement   in  this  event,  Region I

management  initiated  continuous  coverage  of  the  Unit-2  start-up,  to  ensure  that

operators  performed  a  controlled  and  safe  return  of the  unit to  power  operation”

(Richard W. Cooper, II,  Director,  Division  if  Reactor  Projects,  November  21,

1994.)  Severity  Level  IV  Violations  were  issued.

October  21,  1994 - FEMA  assessed  a Deficiency  against the State  of

Maryland  Emergency  Operations  Center  for  communications  failure  during  the

full-participation  exercise  on  August  22,  1994.

- October 24,  1994 - A Licensee Event Report   (LER) was filed for  “Main

Safety  Relief  and  Safety  Valve  Setpoint  Drift.”  (See  May  14  and  November  10,

1 9 9 4 . )

October 27,  1994 - The DER  reported that the  “PECO inspection of the

core  shroud  of  Peach  Bottom-2  did  not  find  any  significant  flaws...Therefore,

there  is no  repair needed for the time  being.” The NRC  stated:  “During the Unit  2

outage  PECO  conducted  an  ultrasonic  inspection  of the  reactor  vessel  core  shroud

accessible  weld  areas.  These  examinations  identified  cracking  of  a  similar  nature

found  at  Unit  3,  but  of much  less magnitude. Based  on  an  engineering  analysis  of

the  examination  results,   PECO  determined that the  Unit  2  shroud  was

structurally  sound  and  that  no  actions  were  required  to  ensure  its  stability  over

the  next  operating  cycle”  (IR  50-277/94-21  &  50-278/94-21.)  (See  June  30,

1994  and  August  18,  1995  for  related  incidents.)

October  31,  1994 - The NRC  reported  “a Senior Reactor Operator (SRO)

entered the  Unit  2  high  pressure  coolant  injection (HPCI) turbine  room,  which

was  visibly  posted  as  a HRA,  and the  individual  was  not  provided  with the

required  alarming  dosimeter,  nor  positive  control  provided  by  an  individual

qualified  in  radiation  protection  procedures,  nor  did  the  individuals  adhere  to

posted  instructions  regarding  entry  requirements,  a  requirement  of  the

Radiation  Work  Permit  under  which  the  entry  was  made”  (IR  50-277/95-05  and

50-278/95-05  and  Notice  of  Violation.)  (See  October  10,  1994,  November  29,

1994  and  March  14,  1995  for  related  incidents  and  a  Notice  of  Violation.)

November  10,  1994 - A LER was filed for  “Non-Conservative Flow Biased

Setpoints.”  (See  May  14  and  October  24,  1994.)

November  18,  1994 -  “A load drop to  about  55% power  occurred  on

November  18,  1994,  to  support  cleaning  of  the  main  condenser  waterboxes.”

Unit-2  returned  to  full  power  the  following  day.  (IR  50-277/94-27  &  50-278/94-

27.)  (See  May  31,July  16,  September  10  and  October  25,  1996;  and,  September

12,  1997  for  related  incidents.)- November  21,  1994 - The NRC  proposed  a  Severity Level III Violation  and

an  $87,500  fine   for  the  emergency  service  water  configuration  problem  on

August  3,  1994.

November  21,  1994 - Three  items  of  weakness  were  noted  by  an NRC

Nondestructive  Examination  Laboratory  Inspection:  “these  were  not  marking

the weld  centerline on welds for UT [ultrasonic inspection]  as part of the ISI

[inservice  inspection]   program,  not  finding  or  recording  a  geometric  reflector  in

excess  of  50%  of DAC [distance  amplitude  correction]  while  conducting UT  per

the ASME [American  Society  of Mechanical Engineers]  code  on  a  RWCU [reactor

water  clean-up]  system  weld,  and  having  radiographs  that  show  signs  of  aging

in  storage  for  work  performed  after  original  construction”  (IR  50-277/94-28  &

5 0 - 2 7 8 / 9 4 - 2 8 . )

November  29,  1994 -  “Two  separate  events  occurred,  involving  a  total  of

five  radiation  workers,  where  personnel  entered  a  high  radiation  area  without

having  the  required  dose  rate  monitoring  equipment.  Individually,  these  events

were  of  low  radiological  consequence;  however,  they  reflect  a  continuing  station

weakness  in  personnel  adherence  to  posted  boundary  requirements  (Section  6.0).

These  events  are  considered  an  Unresolved Item (URI-  94-25-01) (IR  50-277/94-

25  &  50-278/94-25.)

“While  we  recognize  that  you  are  aggressively  taking  actions*  to  prevent

recurrence  the  events  are  similar  in  nature  to  other  recent  radiological  events

for  which  escalated  enforcement  action  was  taken” (Clifford  J.  Anderson,  Section

Chief, Projects Section 2B, Division  of Reactor Projects.) (For  related incidents  see

October  10  and  31,  1994  and  March  14,  1995

*For  similar  events  see March  10,  June  22  and  25,  September  24  and

October  4,  1993  and  January  19,  1994.

- December  9,  1994 -   PECO made  a four  hour  event notification  after the

utility   discovered  two  doors  that  separate  the  main  stack  from  the  environment

were left open for four hours.

December  12,  1994 -  PECO  was  among  a  consortium  of  33  utilities

actively  pressuring  the  Mescalero  Apaches  to  build  a  high-level  radioactive

waste  dump  on  their  land.

December  19-23,  1994 -  An  inspector  “identified  a  condition  where

manual  operation  of fire  protection  system  controls  located  outside  of the  vital

security  areas  could  affect  the  operation  of  vital  safety  systems”  (William  H.

Ruland,  Chief,  Electrical  Section,  Division  of  Reactor  Safety,  NRC,  February  3,

1 9 9 5 . )- December  20,  1994 - An NRC  inspector  determined there  was  poor

control  over  the  use  of  a  non  safety-related  battery  charger  at  Unit-2.

December  22,  1994 -  A  steam/water  discharge  to  the  reactor  building

during  reactor  water  cleanup  system  testing   resulted  in  minor  shoe

contamination  to  three  individuals   and  contamination  in  portions  of  the  Unit-2

reactor  building.

January  7,  1995 -  “Reactor  power  was  reduced to  below  75% [Unit  2]...to

allow for the  repair  of  a  steam leak that developed from the  stem packing  of  an

outboard  MSIV”  (IR  50-277/95-10  and  50-278/95-01.)

February  14,  1995 -   A Violation  was  issued   (Severity  Level IV) for

PECO’s  “failure  to  properly  evaluate  the  installation,  during  outages  in  1993,  of

‘temporary’  shielding  above  each  bank  of  hydraulic  control  units  (HCU)  at  Units

- 2  and  3 (four  locations total),  which  shielding  is till  in  place...your  staff’s

response,  past  and  present,  to  questions  about  the  shielding  arrangements

demonstrated  a  poor  questioning  attitude” (  Clifford  J. Anderson,  Section  Chief,

Projects Section  2B, Division  of Reactor Projects, NRC.)

March  1,  1995 - A High Pressure  Service Leak was identified  by PECO  at

Unit-2.

March  6,  1995  -  “...operational  errors  involving  a  mis-positioned  valve,

an  inadequate  valve  position  verification,  and  poor  communications  resulted  in

the loss of keep fill pressure on the 2B  core  spray (CS)  sub-system [Unit 2.]” (IR

50-277/95-04  and  50-278/95-04.)

March  14,  1995 -  “However,  based  on the  results  of this  inspection,

certain  of  your  activities  were  in  violation  of  NRC  requirements,  as  specified  in

the  enclosed Notice  of Violation (Notice). The  violation is  of  concern  and being

cited  because  of  the  number  of  improper  high  radiation  area  entries  which  are

described  in the  enclosed  inspection  report...in the most  recent  events,

radiological  control  personnel  failed to  carry  out their  assigned  duties  in

accordance  with  radiological  control  management’s  expectations;  no  similar

causal  factors  were  identified  in  the  1993  events.”)  (James  H.  Joyner,  Facilities

Radiological  Safety  and  Safeguards  Branch,  Division  of  Radiation  Safety  and

Safeguards,  NRC.)

March  17,  1995  -  “An  automatic  recirculation  pump  runback  reduced

power [Unit-2] to  about  70%  on March  17,  because  of  a mis-conducted  reactor

feed  pump  test.”  (IR  50-277/95-04  and  50-278/95-04.)  The  incident  was  caused

by  an  operator  error. (See  related  incidents  on March  4,  1996  and May  16  and

June  7,  1998.)- March  19,  1995 - High  Pressure  Coolant Injection (HPCI)  suction  valve

was mispositioned  at Unit-2 due to operator  error. A Notice of Violation   was

issued.  (Severity  Level IV.)  “Also,  two  subsequent  shift  turnover  panel

walkdowns  failed to  identify the  abnormal  system  line-up  and  allowed the  HPCI

system  to  remain  in  the  abnormal  lineup  for  18  hours.” (Clifford  J.  Anderson,

Section Chief, Projects  Section  2B, Division  of  Reactor Projects.)

March  23,  1995  -Unit-3  was  manually  scrammed  “after  the  air-operated

main  steam  supply  isolation  valve to the  ‘B’  steam  jet  air  ejector (SJAE)  failed

closed  causing  a  loss  of  condenser  vacuum.” (IR  50-277/95-08  &  50-278/95-08.)

April  10,  1995 -  “The  inspectors  opened the three  unresolved  items

pending  review  of  your  staff’s  assessment  and  planned  corrective  actions.  The

first  issue  addresses the  possibility that,  due to  an  equipment failure,  a  low

pressure  coolant  injection  sub-system (one  of  four)  was  not maintained  with  its

piping  full  to  prevent  water  hammer  following  an  injection.  The  second  issue

deals  with  the  secondary  containment  flood  control  portion  of  your  emergency

operating  procedures,  which  could  lead  an  operator to flood two  emergency  cool

cooling  pumps  rooms,  a  condition  outside the  plant’s  design  basis. Lastly, the

third  issue  deals  with  inconsistencies  between  the  standby  liquid  control  system

inservice  testing  methodology  and  ASME  Section  XI  requirements  for  pump  run

time  before  operational  data  is  requested.” (Clifford  J. Anderson,  Section  Chief,

Projects  Section  2B, Division  of  Reactor Projects.)

- April  16,  1995  -  All  control  rods  were  “conservatively”  declared

inoperable  at  Unit-2  for  4.5  hours.

April  21,  1995 -  Control  rod  46-07  “unexpectedly  drifted”  out  of  position

at  Unit-2.  (IR  50-277/95-08  &  50-278/95-08.)  (For  related  events  see  June  24,

1993,  February  22,  1994  and  February  15,  1997.)

April  24,  1995  An  unplanned  power  reduction  to  35%  occurred  at  Unit-3

when  the  3B  reactor  recirculation  pump  tripped.  (See  May  13,  1995  for  related

d e v e l o pme n t . )

May  13,  1995  -  The  3B  reactor  recirculation  pump  “unexpectedly”

tripped.   (See April  24,  1995 for   related  incident.)

May  24,  1995  “...several  events  involving  plant  operators  indicate  a

negative  trend  in  plant  operations  performance.  These  instances  include

problems  with  procedural  adherence,  attention  to  detail,  and  control  of

maintenance  activities.”  Executive  Plant  Performance  Results,  Richard  W.

Cooper, NRC, Director, Division  of  Reactor Projects.)-  June  10,  1995  -  “Unplanned  Engineered  Safety  Feature  Actuation

During  Diesel  Testing”   caused  a  Licensee  Event  Report. (IR  50-277/95-15  &  50-

2 7 8 / 9 5 - 1 5 . )

- June  13,  1995 -  The  calibration  check  of the  Feedwater Inlet

Temperature  instruments  utilized  equipment  that  was  later  “found  out  of

tolerance.”  (IR  NOS.  50-277/98-01  AND  50-278/98-01.)

June  18,  1995 -  “Condition  prohibited  by TS when two EDGs  were

Inoperable  at the  same time”  caused  a  Licensee Event  Report.   (IR  50-277/95-15

&  50-278/95-15.) (See  August  17,  1995  for  proposed  fine.  Related  incidents  begin

on  December  10,  1996.)

June  29,  1995 -  “During  the  conduct  of  troubleshooting  an  electrical

ground  on the  Unit  3  station  battery,  we  noted  an  apparent  lack  of  attention to

detail  and  questioning  attitude  on the  part  of  your  staff.” (Glenn W. Meyer,

Chief, BWR & PWR, Division of Reactor Safety, NRC.)

July  6,  1995 - A Licensee Event  Report  occurred  when  due to  a,  “High

Pressure  Coolant  Injection  System  Valve  Motor  Failure.”

July  10,  1995 -  The  NRC  accepted the following  changes  at  Peach Bottom,

“...  eliminating  the  Independent   Safety  Engineering  Group  composition

commitment  while  retaining  the  independent  technical  review  function,

relocating  Nuclear  Review  Board  requirements,  and  reducing  the  frequency  of

certain  nuclear  quality  assurance  audits.”   (Michael  C.  Modes,  Chief,  Materials

Section,  Division  of  Nuclear  Safety,  Nuclear  Regulatory  Commission.)

July  17,  1995 -  “Inspector  review  of the  E-2  and  E-4  emergency  diesel

generator  modifications  indicated  that  pre-existing  drawing  errors  [see  April  30,

1993]  and  insufficient  post-modification  testing  caused  both  operating  reactor

units to  be  placed  in  a  situation  where  only two  emergency  diesel  generators

(i.e., E-1  and E-3  operable; E-4  in  a maintenance  outage,  while the  E-2  output

breaker  would  not  automatically  close)  remained  able  to  automatically  respond

to a loss of off site power or a design basis accident condition. The inspectors also

identified that inadequate  review of the modification led to  a loss of power of  an

emergency  power  bus  during  testing,  and  the  introduction  of  a  design  flaw  such

that  E-2  and  E-4  were  not  able  to  automatically  perform  their  safety  functions...“The  emergency  diesel  generator modification  issues  are  of  concern to  us

since  your  normal  design  and testing  process  did  not  uncover  a  basic  error that

would  have  led  to  the  E-2  and  E-4 machines  being  unknowingly  inoperable.  This

condition  could  have  remain  unknown  until  challenged  or  until  the  Unit  3  Fall

1995 post outage loss of off site power testing. Based on these  results of the

inspection,  three  apparent  violations  were  identified  and  are  being  considered  for

escalated  enforcement  action...”   (Richard W. Cooper II,  Director,  Division  of

Reactor  Projects,  NRC.)

(See  August  17,  1995,  for  enforcement  information.)

July  21,  1995 -  The  NRC’s  review  of  PECO’s  emergency  preparedness

plans  at  Limerick  and  Peach  Bottom  found:  “...quality  control  was  lacking  for

Emergency Plan [EP]  and procedure  revisions,  as the  omission  of  a portion  of  an

essential  paragraph,  concerning  public  emergency  information,  as  well  as

numerous  other minor  errors,  was found. Inspectors  also  noted that the  corporate

EP  staff had no documented plan in place to  carry  out the EP training  of

corporate  emergency  responders.”  (James  H.  Joyner,  Chief,  Facilities

Radiological  Safety  and  Safeguards  Branch,  Division  of  radiation  safety  and

safeguards,  NRC.)

July  30,  1995 -  Unit-3  scrammed  “on  high  reactor  water  level  due to  a

control  signal  failure  for  the  3A  reactor  feed  pump.” (IR  50-277/95-15  &  50-

278/95-15.)  (See  November  6,  1995  for  a  related  incident.)

August  9,  1995 -  An  Unusual  Event  was  declared  for  a  “potentially

contaminated  injured  man  being  transported  off-site  by  ambulance...”  (IR  50-

277/95-15  &  50-278/95-15.)

August  13,  1995 -  PECO  identified  excessive  average  control  rod  scram

times  at  Unit-3.

- August  14,  1995 -  PECO failed to meet technical  specification

requirements  when  a  Reactor Water  Clean-up  temperature  switch  was  found  to

be  inoperable.

August  15,  1995 -   The NRC determined a partial loos of off-site power was

cause  by  poor  maintenance  activities.

- August  17,  1995 - The NRC proposed  a $50,000 fine for the Severity

Level III  violation  associated  with  EDGs  identified  on  July  17,  1995.

August  18,  1995 -  “HPCI [High  Pressure Coolant Injection  steam  lines]

system  piping  in  both  units  is  experiencing  high  vibration  levels  due  to  unknown

causes.”  (IR  50-277/95-18  &  50-278/95-18.)-  August  18,  1995 -  The  NRC  identified  a  crack  about  3” (length)  by  2.5.

“...The  crack  is  believed  to  be  caused  by  intergranular  stress  corrosion (IGSC).”

(IR  50-27/95-18  &  50-278/95-18.)  Rich  Janati  of  the  Pennsylvania  Department

of  Environmental  Protection  stated,  “...the  new  cracks  are  not  exactly  on  the

core  shroud.  They  are  on  the  core  spray  line.” (September  5,  1995.) (See  June

30,  1994  and  October  27,  1994  for  related  incidents.)

August  24,  1995 -  During  the  disassembly  of  a  transversing  incore  probe

(TIP), the  NRC  “identified  weaknesses  in  personnel  communications,

understanding  of  radiological  conditions  associated  with  the  work  activity,

supervisory  oversight,  and  control  of  contractor  work  activities.  (See  March  10,

June  22  and  25,  September  24,  October  4  and  November  4,  1993  and  June  19

and  November  29,  1994).  Four  examples  of  personnel  failing  to  adhere  to

radiation  protection  procedures,  a  violation  of  NRC  requirements  [Severity  Level

IV],  were  identified.”  James  H.  Joyner,  Chief,  Facilities  Radiological  Safety  and

Safeguards  Branch,  Division  of  Radiation  Safety  and  Safeguards,  NRC,

September  22,  1995.)  (See  March  10,  1993  for  a  related  incident.)

August 25,  1995 - Reactor power was  reduced  at Unit-3 to 30% due to  a

problem  with  a  main  turbine  control  valve.

September  22,  1995  -  At  Unit-3  “an  unexpected  reactor  recirculation

pump (RRP) motor  generator (MG)  set trip  occurred  due to  a maintenance

technician  inadvertently  bumping  a  loose  resistor  lug  in the  RRP  in the  RRP MG

control  cabinet.”  (IR  50-277/95-22  &  50  2787/95-22.)  (See  May  14,  1995.)

- October  18,  1995 -  Excessive  scram times  were  identified  at  Unit-3.

October 20,  1995 - Results of  examinations of  senior  reactor operators

“reflect  an  unexpected  poor  level  of  performance  in  the  simulator.” (Michael  C.

Modes,  Acting  Chief,  Operator  Licensing  and  Human  Performance  Branch,

Division  of  Reactor  Safety,  NRC.) (See  December  27,  1995  for  follow-up  report.)

October 22,  1995 - Power was  reduced to 90% at Unit-2  “in  response to a

loss of feedwater heating  caused by  a partial loss of offsite power. During the

recovery  from  this  event,  PECO  discovered  that  an  existing  ‘5B’  feedwater  heater

(FWH)  leak  had  degraded.  PECO  returned  reactor  power to  100%  until  October

26, when PECO  reduced power to 68% to isolate the  ‘B’ FWH train  and then

limited Unit  2  power  operations to  95%  power. On November  4, PECO  declared

the  ‘C’  safety  relief  valve  inoperable  because  of  a  leaking  bellows.  On  November

7,  PECO  returned  the  unit  to  100%  power  after  completing  a  safety  evaluation

allowing  full  power  operation  with  one train  isolated.  Full  power  operations

continued  until  November  20,  when  PECO  reduced  power to  95% to minimize

vibration  of  the  2A  reactor  feed  pump  (RFP).”  (IR  50-277/95-26  &  50-278/95-

2 6 . )-  October  27,  1995 - An  NRC  inspection  found two, technical  unresolved

issues:  1)...Peach  Bottom  fire  protection  program  and  the  impact  of  inadvertent

discharge  of CSR (cable  spreading  room)  carbon  dioxide  system  on the  installed

safety  equipment;  and  2)...the  appropriateness  of  Peach  Bottom’s  response to  an

inadvertent  carbon  dioxide  discharge  alarm.”  (IR  50-277/95-24  &  50-278/95-

2 4 . )

November  6,  1995 -  At  Unit-3,  an  “unexpected”t  trip  occurred  at  the  ‘3A’

circulating  water  pump.  (See  September  2,  1997  and,  January  14,  1998,   for

related  incidents.)

December  2,  1995 -  A main turbine  trip  caused  a  full  reactor  scram  at

100%  power   Unit-3.

December  5,  1995 -  On  September  22,  1995 A  Notice  of Violation  was

issued  relating to  PECO’s  “failure to  adhere to  radiation  protection

procedures...We  have  evaluated  your  response  to  the  violation  and  found  that

you  have  not  completely  responded  as  required  by the  Notice  of Violation. While

your  response  identifies  immediate  actions that  were taken,  it  does  not

adequately  address  generic  and  long-term  actions  to  prevent  recurrence.  For

example,  you  indicate  that  a  Performance  Enhancement  Process  (PEP)

investigation  was  initiated  to  determine  the  causes  and

reasons for the  contamination  event,  and that   the  actions taken  as  a  result  of

that  effort  are  expected  to  prevent  recurrence.  However,  you  have  not  indicated

what  the  findings  of  that  effort  revealed (i.e.,  what  were  the  causes  and  reasons),

and  what  consequent  corrective  actions  were  implemented  to  address  those

factors.  Further,  you  indicated  that  a  Quality  Improvement  Team  (QIT)

performed  an  evaluation  of  the  work  process,  and  their  recommendations  will

improve  radiological  and  work  control.  However,  you  did  not  provide  any

discussion  of  what  recommendations  were  implemented  and  how   improved

performance  will  be  be  achieved.”   (James  T. Wiggins,  Director,  Division  of

Reactor  Safety,  NRC,  December  5,  1995.)

December  12,  1995 - A  Severity Level IV Notice  of Violation  was  issued

due to  PECO’s failure to monitor  drywell  leakage  at  Unit -3.   “Specifically,  a

modification  prepared  by  your  engineering  staff  lead  to  the  installation  of

drywell  drain  tank  pump  control  instrumentation  that  did  not  function  as

designed.  Further,  post-maintenance  testing  should  have  identified  the  problem

and  did  not.  Operators  also  initially  failed  to  identify  that  the  drywell  pumps

were  not  functioning,  based  on  changes  in  in  the  calculated  drywell  leakage.”  A

similar  incident  occurred  in  October  1994  at  Unit-2  according  to  the  NRC.

(Walter  J.  Pasciak,  Section Chief,  Projects Branch  4,  Division  of  Reactor  projects,

NRC.)   (See   November  16,  1992  for  a  related  incident.)- December  27,  1995 -   On December  14,  1995, PECO  and the NRC held  a

meeting to  determine the  causes  of  “weak  performance”  on  operator  exams. (See

October  20,  1995.)  The  Company’s  conclusions  included  “...  the  unrecognized

need for  senior  reactor  operator (SRO)  candidates to  have  additional  plant

familiarization,  the  weak  understanding  of  system  details  including  protection

and  control  logic, the  need to  upgrade the  cognitive  level  of  written  questions,

and  the  infrequent  evaluation  of  the  candidates’  ability  to  prioritize  mitigating

actions  during  simulator  scenarios. In  addition,  your  staff  stated  that  your

guidance  for  examination  validation  and  proadministration  review  will  be

revised  to  promote  prompt  escalation  of  any  unresolved  examination  concerns  to

PECO  Energy  management.”  (Glenn  W.  Meyer,  Chief  Operator,  Licensing  and

Human  Performance  Branch,  Division  of  Reactor  Safety,  NRC,  December  27,

1 9 9 5 . )

January  20,  1996 -  Power  reduced  at  both  units  due to the  high  river

l e v e l .

January  30,  1996  -  The  NRC  praised  the  radioactive  waste  program  but

“noted  weaknesses  in  training  provided  shipping  personnel  on  radioactive

material  hazards  and  considered  this  an  unresolved  item.”  (Walter  J.  Pasciak,

NRC, Chief Projects Branch 4, Division  of  Reactor Projects.)

February  1,  1996 -  Power  was  reduced  at  Unit  3  “for  condenser  water  box

cleaning.  (IR  50-277/96-01  &  50-278/96-01.)

February  2,  1996 -  Plant  operators  “identified  a  hydrogen  leak  on the

Unit  3  generator  neutral  bushing.  Operators  reduced  power  to  23%  to  remove

the  generator  from  the  grid  and  effect  repairs.”  (IR  50-277/96-01  &  50-278/96-

0 1 . )

February  3,  1996 - At Unit-2, power was  reduced to  “85% for  repair  of  a

hydraulic  control  unit  and  rod  pattern  adjustment.”  (IR  50-277/96-01  &  50-

2 7 8 / 9 6 - 0 1 . )

February  5,  1996 - Power was  reduced  at Unit 2 to  78%  “in  response to  a

loss  of  condenser  vacuum  event...”  (IR  50-277/96-01  &  50-278/96-01.)

March 4,  1996 - Power was  stabilized  at 65% power  at Unit  2  after  “a

recirculation  pump  runback  due  to  the  2B  reactor  feedwater  pump (RFP)  trip.”

(IR  50-277/96-01  &  50-278/96-01.)  (See  related  incidents  on  March  17,  1995

and  May  16  and  June  17,  1998.)- March  25,  1996 - The NRC  issued two  violations  during  a  routine

inspection.  “They  involved  not  properly  performing  functional  testing  of  the

safety-related  degraded  grid  under  voltage  relays  to  ensure  their  operability,

and  inadequate  controls  over  a  125  vdc  circuit  breaker  supplying  power  to

portions  of the  Unit  2  remote  shutdown  panel.” (Walter  J.  Pasciak,  NRC, Chief,

Projects  Branch  4,  Division  of  Reactor  Projects.)   (See  April  24,  1996.)

April  17,  1996 - The  Unit-2  “High  Pressure Coolant Injection (HPCI)

system  was  declared  inoperable  and  removed  from  service  following  the

discovery of  a  10 drop per minute leak from the inlet nipple of the HPCI  cooling

water  line  relief  valve.”  (IR  -277/98-02; 50-278/98-02.)

- April  24,  1996 -  Two  Severity  Level IV  violations  were  issued  by the

NRC.  “...since  1989,  PECO  had  calibration  data  that  indicated  that  the  98%  and

89% degraded  bus under  voltage  relay  setpoints were found to  be  outside  of the

Technical  Specification  allowable  values  and  did  not  take  appropriate  actions  to

the  correct the  issue...Contrary to the  above,  PECO  did  not  properly  identify  or

implement  corrective  actions  to  identify  and  correct   an  adverse  circuit  breaker

position that  caused portions  of the Unit 2 Remote Shutdown panel to not  receive

alternate  control  power  for  over  a  year.  This  failure  led to  several  functions  of

the  remote  shutdown  panel  being  inoperable  from  October  1994  through

January  1996.”  (PECO  Nuclear,  Thomas  N.  Mitchell,  Vice  President,  Peach

Bottom  Atomic  Power  Station.)  (See  March  25,  1996.)

Spring,  1996 -  PECO  Energy  Company  has  expressed  interest  in  an

Energy  Department  proposal  to  use  fuel made  from  decommissioned  warheads  at

Peach Bottom  and Limerick.   Peco  spokesman William  Jones  stated,  “It is just

something we’ve  expressed interest, if the DOE picks up the  cost  and there is  a

net  benefit  for  our  customers.”  But  Greenpeace  spokesman  Tom  Clements

observed,  “Consumers  now  will  be forced to  produce  bomb material  and

encourage  international  plutonium  use  by  simply  flipping  their  light  switch.”

All  told,  eighteen  utilities,  including  a  Canadian  entity,  are   interested  in  using

fuel  made  from  weapons-grade  plutonium. (From U.S.  Newswire, Greenwire and

The Houston Chronicle.)

May 9,  1996 - Power was  reduced to 65%  at Unit   2 due to turbine  control

valve  (No.  2)  failure.

May 9,  1996 - An Notice of Violation was issued when  “Control Room

Emergency  Ventilation  Filter  Train  ‘A’  Test,  was  identified  as  being  out  of

sequence.”  (NRC,  August  6,  1996.) - May  31,  1996 - Power was  reduced  at Unit  3 to  62%  “to  allow  condenser

waterbox  cleaning,  control  rod  pattern  adjustments,  and  other  preventive

maintenance  activities.”  (IR  50-277/96-04  and  50-278/96-04.)  (See  November

18,  1994; July  16,  September  10  and  October  25,  1996; and,  September  12,

1997  for  related  incidents.)

May 22,  1996 - A Notice of Violation was issued for   “...an unexpected loss

of the Unit  2  ‘B’  RPS power  supply  occurred when  an  equipment  operator

mispositioned  the  voltage  adjustment  rheostat  for  the  ORS  Alternate  feed

transformer.”  (NRC,  August  6,  1996.)

June 3,  1996 - The NRC notified PECO that  “we  are unable to  close  your

NRC  Generic  Letter  89-10  motor  operated  valve  program  at  this  time.”   (Walter

J.  Pasciak,  NRC, Chief,  Projects Branch  4,  Division  of  Reactor  Projects.)

June  9,  1996 - Power was  reduced to  71.5%  at Unit  2  “to  secure the  2C

reactor  feed  pump  (RFP)  for  scheduled  maintenance.” (IR  50-277/96-04  and  50-

2 7 8 / 9 6 - 0 4 . )

June  12,  1996 -  “...the  hatch  between  the  Unit  #3  refuel  floor  and  the

refuel floor roof was propped open to allow access to the roof for

performance...Personnel  performing  this  test  believed  that  the  only  procedural

requirement   to  open  the  hatch  was  to  have  a  security  guard  present.”  (August

6,   1996. )

June  22,  1996 - Power was  reduced to  25%  at Unit  3  “to  repair  electrohydraulic  control (EHC)  oil  leaks  on the  No.  4  TCV [Turbine  Control Valve]  and

No.2  TSV.”  (IR  50-277-96-04  and  50-278/96-04.)  (See  June  23,  1996  for

related  incident.)

June  23,  1996 -  “Manual  unit  shutdown  and  forced  outage [Unit  3],

during the  June  22  load  drop the  No.  2  TCV [Turbine  Control Valve]

mechanically  failed.  PECO  completed  the  outage  and  restarted  the  unit  on  June

27,  the  unit  reached  100%  on  June  28.  (See  June  22  1996  for  related  event.)

July  16,  1996 -  Power  was  reduced to  72%  at  Unit-3 for main  condenser

waterbox  cleaning.  (See  November  18,  1994; July  16,  May  31,  September  10

and  October  25,  1996;  and  September  12,  1997  for  related  incidents.)

August  2,  1996 - Power  was  reduced to  70%  at  Unit-3  “to transfer the

steam  jet  air  ejectors  and  repair  a  steam  leak from the  packing  of the  steam

isolation  valve.”  (IR  50-277/96-06  and  50-278/96-06.)  (See  August  10,  1996

for  a  related  incident.)- August 6,  1996 - A Notice of Violation was issued  after NRC inspectors

“noted  three  examples  where  station  personnel  performed  activities  without

properly  implementing  the  established  written  procedures.  These  procedural

adherence  deficiencies  involved  various  parts  of  the  site  organization  and

indicated  a  decline  in  station  procedural  adherence.” Walter  J.  Pasciak,  NRC,

Chief, Projects Branch  4, Division  of  Reactor Projects.

August 6,  1996 - Power was  reduced to 85%  at Unit-3  “in  response to  an

off-gas  recombiner  isolation.”  (IR  50-277/96-06  and  50-278/96-06.)

August  10,  1996 - Power was  reduced to  55%   at Unit-3  “to transfer the

steam  jet  air  ejectors.”  (See  August  2,  1996  for  a  related  incident.)

September  1,  1996 -  “...the  Company’s  stock  price  under  performed  the

Dow Jones Utilities Index and S&P 500 Stock Index due to the forced shutdown of

Salem  Units  No.  1  and  No.  2,  uncertainty  about the  pace  of  competition  in

Pennsylvania  and  the  decline  in  1996  earnings  [down  $0.24  per  share.]”

(“Report  to  Shareholders,  “  J.F.  Paquette,  Jr.,  Chairman  of  the  Board.)

September  5,  1996 - PECO joined  a  consortium of utilities  asking the DOE

“to consider them as candidates for the disposal of U.S. and Russian  stockpiles of

weapons-grade  plutonium...Under  the  proposal,  the  utility  companies  would

burn fuel  pellets  hat  include  small  amounts  of  plutonium  oxide  in  addition to the

pellet’s  traditional  ingredient,  uranium  oxide...”  (AP,  September  5,  1996.)

September  10,  1996  -  Unit-3  “...unit  load  was  reduced  to  approximately

75%  power  for  condenser  water  box  cleaning.” (See  October  25,  1996,  for  related

incident.)  (IR  50-277/96-08  &  50-278/96-08.)

- September  20,  1996  -  “...with  Unit  3  shutdown,  the  maintenance

personnel  mistakenly  pulled  the  primary  containment  isolation  system  (PCIS)

inboard  and  outboard  mechanical  vacuum  pump  trip  logic  fuses...while  working

on  a  local  leak  rate  test  activities”.  (IR  50-277/97-04  &  50-278/97-04).

October  1,  1996 -  The  Nuclear  Regulatory  Commission (NRC)  fined

Thermal  Science, Inc.  (TSI)  $ 9 0 0 , 0 0 0 for  “deliberately  providing  inaccurate  or

incomplete  information to the  NRC  concerning  TSI’s  fire  endurance  and

ampacity  testing  programs.”  (James  Lieberman,  Director  of   Enforcement.)   The

fine  was the  largest  assessed  against  a  nuclear  contractor  and the  second  highest

in  the  agency’s  history. In  1992,  the  NRC  declared  TSI’s  fire  barrier,  ThermoLag,  “inoperable.”  (For  related  incidents,  see  December  18,  1993,  September  29,

1994,  May  19,  1998,  October  12,  1999,  and  July  21,  2000.)

October  6,  1996 -  Unit-2  scrammed  due to  equipment  problems. (See

October  15,  1996  for  a  related  incident.  Also,  see  November  18,  1994  and  May

31  and  July  16,  1996  for  related  problems.)- October 9,  1996 -  “Based  on the  results  of this inspection,  an  apparent

violation  was  identified  and  is  being  considered  for  escalated  enforcement

action...Specifically,  the  failure  to  establish  adequate  performance  criteria  that

would  demonstrate  appropriate  preventive  maintenance  for  several  systems  and

components  was  identified.” (NRC,  James  T. Wiggins,  Director  Division  of

Reactor  Safety.)

October  10,  1996 -  “The  violation  deals  with  your  procedures  allowing

operation  of  the  [standby  gas  treatment]  system  that  was  unanalyzed  in

accordance  with  the  updated  final  safety  analysis  report...”  A  predecisional

enforcement  conference was  also  announced.   (NRC, Richard W. Cooper, II,

Director,  Division  of  Reactor  Projects.)

October  15,  1996 - Unit-2  scrammed for the  second time  in nine  days  due

to  equipment  problems.

October 25,  1996 -   Unit-3  “...unit load was  reduced to  about  58% for

waterbox  cleaning,  control  rod  drive  scram  testing  time,  and  3A  reactor  feed

pump  maintenance.”   (See  September  10,  1996   for  a  related  incident.  Also,  see

November  18,  1994;   May  31  and  July  16,  1996;  and,  September  12,  1997  for

related  problems.)  (IR  50-277/96-08  &  50-278/96-08.)

October 29 -  1996 - Unit-3  “power was  reduced to about 60% power to

mitigate  a  lowering  condenser  vacuum  condition  which  developed  due  to  off-gas

recombiner  system  problems.”  (IR  50-277/96-08  &  50-278/96-08.)

- December  10  and  27,  1996 -  Emergency  diesel  generator  power

fluctuations  were  reported.  (IR  50-277/97-01  &  50-278/97-01.)  (See  December

27,  1996  and  January  24,  February  7  and  March  6,  1997  for  related

de v e lopment s . )

- December  18,  1996 -  The  NRC  recognized two,  Severity  Level IV

violations  during  an  inspection  from  September  8,  through  November  9,  1996:

“The  first  issue  involved  the  failure  to  maintain  an  adequate  contractor

qualification  program,  to  ensure  the  qualification  of  contractor  personnel

performing  independent  safety-related  work  activities.  The  second  issue  involved

the  failure  of  engineering  and  operation  personnel  to  identify  and  prevent  the

calibration  of  average  power  range  monitors  outside  of  the  technical  specification

limits.  This  resulted  in  a  failure  to  enter  a  technical  specification  required

shutdown  action  statement  for  inoperable  average  power  range  monitors.”

(Walter  J.  Pasciak,  NRC,  Chief,  Projects Branch  4,  Division  of  Reactor  Projects.)-December  20,  1996 -  “Based  on the  results  of this  inspection,  an  apparent

violation  was  identified  and  is  being  considered  for  escalated  enforcement...The

apparent  violation  concerned  the  failure  to  control  safeguards  information  in

accordance  with  NRC  requirements.  The  circumstances  surrounding  this

apparent  violation, the  significance  of the  issue,  and the  need  for  lasting  and

effective  corrective  action  were  discussed  with members  of  our  staff  at the

inspection  exit  meeting  on  November  27,  1996.”  (James  T.  Wiggins,  Director,

Division  of  Reactor  Safety,  NRC,  December  20,  1996.)

December  27,  1996 -  The  NRC  cited  PECO for  a  violation  involving the

failure  to  verify  a  modification  change  on  an  emergency  diesel  generator.  (IR  50-

277/96-06  &  50-278/96-06.)  (See  December  10,  1996  and  January  24,

February  7  and  March  6,  1997  for  related  developments.)

January  3,  1997 - A  Severity  Level III Violation  was  issued  by the  NRC

for  “the  failure  to  establish,  for  several  structures,  systems,  and  components

(SSC),  adequate  performance  criteria  to  monitor  the  effectiveness  of  preventive

maintenance...Since  this  violation  involved  multiple  examples  of  failures  to

establish,  or  adequately  establish,  performance  criteria...the  violation  has  been

categorized  at  Severity  Level  III...”  (NOV  50-277/96-07  &  50-278/96-07.)

January  8,  1997  -FEMA  identified  several  deficiencies  during  the

emergency  preparedness  drill  on  November  19,  1996  including:  coordination  of

information  with  the  York  County  Communication  Center  and  the  county’s

emergency  management  staff  and  the  failure  of  the  Cecil  County  Emergency

Operations  Center  to  notify  the  public  promptly  and  maintain  the  proper

notification  sequence.

January  21,  1997  -  NRC  inspectors  determined  that  core  thermal  power

was  operating  at  a  rate  greater  than  mandated  in  the  technical  specifications

since  June  12,  1995,  due  to  improperly  calibrated  feedwater  temperature

instruments.  (IR  50-277/97-01  &  50-278/97-01.)  “Thus,  this  issue  represented

a  missed  precursor  event.”   (June  4,  1997,  IR  50-277/97-02  &  50-278/97-02.)

January  21,  1997  -  High  Pressure  Coolant  Injection  stop  valve  timing

and  gland  condenser  gasket  failure  was  reported  at  Unit-3.  A  similar  event

occurred   in  August  1996.  (IR  50-277/97-01  &  50-278/97-01.)

January  24,  1997 -  PECO  declared the EDG [E1]  inoperable  due to

observed power  swings  of 200 to 300 KW while increasing load,  500 KW  at  rated

load,  and  a  500  KW  during  shutdown.”  (IR  50-277/97-01  &  50-278/97-01.)

(See  December  10  and  27,  1996  and  February  7  and   March  6,  1997  for  related

de v e lopment s . )-  February  1,  1997  -  “...an  unexpected  reactor  water  conductivity

increase  “  followed  a  “load  drop.”  (IR  50-277/97-01  &  50-278/97-01.)

February  7,  1997  -  An  “unresolved  item”  was  identified  during  an

inspection  “dealing  with  your  staff’s  inability  to  identify  the  cause  of  load

fluctuations  on  the  E-1  emergency  diesel  generator  during  testing  operations.

This item was of  concern  since, without  a  root  cause, the possible  affects on

operability  may  not  be  clearly  identifiable.”  (Walter  J.  Pasciak,  NRC,  Chief,

Projects  Branch  4,  Division  of  Reactor  Projects.) (See  December  10  and  27,  1996

and  February  7  and  March  6,  1997  for  related  developments.)

February  10,  1997 -  Two  violations  were  identified  in  the  turbine

building.  “These  violations  involved  failure  to  assure  that  the  turbine  building

atmosphere  was  processed  through  the  turbine  building  gaseous  waste  treatment

system  as  specified  in the  ODCM,  and failure to  provide  an  adequate  safety

evaluation  to  support  certain  aspects  of  the  modification  in  accordance  with  10

CFR  50.59.”   (John  R. White,  NRC, Chief,  Radiation  Safety Branch,  Division  of

Reactor Safety.) (See May 7, 1997, for NRC rebuke on PECO’s lack of followu p. )

February  15,  1997  -  “...with  Unit-3  at  100%  of  rated  power,  while

performing [a  control  rod  exercise], the  reactor  operator (RO)  selected  control  rod

58-39  and moved  it  in,  from  position  48  to  46.  Subsequently,  after  becoming

distracted  by  a  telephone  call,  the  operator  returned  to  the  test  and  mistakenly

moved  control  rod  58-43,  from  position  48  to  46,  without  first  returning  control

rod  58-39  to  position  48.”  (IR  50-277/97-01  &  50-278/97-01.)  (For  related

events  see  June  24,  1993,  February  22,  1994  and  April  21,  1995.)

- February  27,  1997 -  “PECO  Energy Inc.  had  a  yield  of  7.44

percent...Those  are  stocks to  be  avoided”  because these  companies  are  high-cost

producers that may  not  be  able to  afford to  keep  paying their  dividends,  said

Miller,  who  manages  the  Better  Than  Bonds/Utility.’  (Dow  Jones  News  Service.)

March  1997 -  “Common  stock  earnings  for  the  year  ended  December  31,

1996,  were  $2.24  per  share,  $0.40  per  share  lower  than  last  year.”  (PECO

Energy,  “Report  to  Shareholders”,  J.  F.  Paquette,  Jr.,  Chairman  of  the  Board.)

March  6,  1997 - On March  6,  operators  declared the E-3 EDG inoperable

because  of  observed  fluctuations  in  generator  output  load...”  (IR  50-277/97-01  &

50-278/97-01.)  (For  related  developments  see  December  10  and  27,  1996  and

January  24  and  February  7,  1997.)

March  9,  1997 -  A  manual  reactor  scram  was  initiated  at  Unit  3  “...as

operators  lowered  reactor  power to  allow  a  drywell  entry to  correct the  low  lube

oil  level,  the  A  recirculation  pump  tripped...”  The  reactor  returned  to  operation

three  days  later.  (IR  50-277/97-02  &  50-278/97-02.)- March  24,  1997 -  The  Dow  Jones  utilities  average  “has  dropped  8.1

percent  since  reaching  a  52-week  high  in  late  January  on  the  expectation  that

the  Fed  will  soon  raise  interest  rates,  investors  said.  Niagara Mohawk  Power

Corp., PECO Energy Corp. and Unicom Corp. led the drop. The Dow Jones

Industrial  average,  meanwhile,  is  little  changed  for  that  period.”  (Bloomberg

Business  Service.)

- March  25,  1997  -  Inadvertent  shutdown  of  Unit-3  drywell  chiller

occurred.  (See  August  22,  1998  for  a  repetitive  incident.)

April  1,  1997 - At Unit  2,  “Reactor  power  was  reduced from  100% to

approximately  48%  due  to  a  leak  at  a  main  turbine  control  valve  (TCV)  drain

line.”   (IR  50-277/97-02  &  50-278/97-02.)

In  addition,  “...  the  2’  A’  Reactor  Feedwater  Pump  Turbine  high  water

level  trip  capability  was  inoperable  for  greater  than  two  hours  while  Unit  2

reactor  power  was  [greater  than]  25%.”  (IR  50-277/98-03;  50-278/98-03.)  The

NRC  issued  a  Level IV  violation. (Also,  see  November  7,  1997, for  a  similar

incident.)

April  1,  1997 - PECO filed its  Restructuring Plan with the PUC  and  asked

to  recover $6.8 billion  in  “uneconomical”,  stranded  costs.  The  initial  proceeding

will  deal  with  a  request  for  $3.7  billion. (See  April  14, May  22  and  June  18,

1997,  for  more  information.)

April  10,  1997 -   Unit  3   was  operating  at  100%  power when  “the B

recirculation  pump  tripped  unexpectedly  due  to  a  fault  to  ground  the  power

cabling  to  the  motor  generator  set.”   (IR  50-277/97-02  &  50-278/97-02.)

April  14,  1997 -  “PECO  entered  a two hour TS  actions (TSA)...for loss  of

the C  reactor feed  pump (RFP)  high  water  level trip  capability  on Unit  3  due to

the  discovery  of  a  blown fuse. The  blown fuse made the trip function,  required TS

3.3.2,  inoperable.”  (IR  50-277/97-02  &  50-278/97-02.)

April  14,  1997 - Administrative  Law  Judge  Louis  Cocheres  issued  a

decision  stating  PECO  was  not  entitled to  recoup  and  “stranded  assets”  primarily

associated  with  its  nuclear  generating  stations  at  Limerick  and  Peach  Bottom.

(Associated  Press,  April  14,  1997.) ((See  April  1, May  22   and   June  18,  1997  for

more  information.)

April  15,  1997 - A  high  pressure  water  service  system   leak  developed   at

Unit 3.  “The  size  of the hole was determined to be  about 2 mm in diameter,  and

the  leak  rate  was  less  than  1  gallon  per  minute.” (IR  50-277/97-02  &  50-

2 7 8 / 9 7 - 0 2 . )- May  7,  1997 - A  follow-up Inspection  dealing  with  violations  identified  by

the  NRC  on  February  10,  1997,  found  that  PECO  failed  to  provide  data:

During  the  telephone  discussion  we  conveyed  several  concerns

with the [PECO’s]  response.  Principally, the  discussion  of  reasons

for the  violations  did  not  clearly  identify  root  or  proximate  causes.

Accordingly,  we  could  not  conclude  that  corrective  actions  you

specified  effectively  addressed the  cause  of the  violation.

Additionally,  your  response  indicated  that  your  safety  evaluation

was  based  on  the  premise  that  the  Turbine  Building  was

maintained  at  a  negative  pressure  so that  air  would  not  be

expected  to  be  released  through  the  penetrations.  However,

no  information  was  provided  as to  why  the  Turbine  Building  was

not  maintained  at  a  negative  pressure,  as  presumed  by  your

safety  evaluation.  Further,  no  commitment  was  made  to

document   and  report  your  estimate  of  the  unmonitored  release...

(James T. Wiggins, NRC, Director, Division of Reactor Safety.)

May  9,  1997 -  PECO  entered  into  an  agreement  with  Delmarva  Power  &

Light  Company  and  Public  Service  Electric  and  Gas  Company (PSE&G)

regarding the  shut  down  of the  Salem  nuclear  power  plant.  “Under the terms  of

the  settlement,  PSE&G  will  pay  the  Company [PECO]  $69.8  million  and

Delmarva  $12.1   million.  The  settlement  also  provides  that  if  the  current  outage

exceeds  64  reactor  unit months,  PSE&G  will  pay the two  companies  an

additional  $1.4  million  per  reactor  unit  month,  up  to  an  aggregate  of  $17

million,  to  be  divided  proportionately.  A  reactor  unit  month  is  a  month  during

the  current  outage  in  which  a  unit  is  off-line. (J.  F.  Paquette,  Jr.,  Chairman  of

the  Board,  “Report  to  Shareholders,”  June  1997.)

May  22,  1997 -  The  PUC  ignored  the  recommendation  of  Administrative

Law  Judge Louis Cocheres  and  allowed PECO to  recoup $1.1 billion in  stranded

investments  from  customers.  As  part  of  Negotiated  Settlement  worked  out

between  PECO  and  intervening  parties  and  approved  by the  PUC,  PECO  was

awarded $5.4 billion in  “stranded  costs”.   (For more information  see April  1

&  14  and  June  18,  1997.)

June  1997 -  “Common  stock  earnings  for  the  quarter  ended March  31,

1997,  were  $0.49  per  share,  $0.16  per  share  lower  than  the  earnings  of  $0.65

per  share  for  the  first  quarter  of  last  year...Earnings  for  the  twelve  months

ended March  31,  1997  were  $2.08  per  share  as  compared to  $2.64  per  share  for

the  corresponding  period  in  1996.” (J.  F.  Paquette,  Jr.,  Chairman  of  the  Board,

“Report  to  Shareholders,”  June  1997.)-  June  4,  1997 -  Two  violations  were  identified  by the  NRC  including

failure  to  full  “understand”  or  “review”  the  significance  of  a  reactor  feed  pump

trip  and  temporary  scaffolding  was  located  too  close  to  safety-related  equipment.

June  5,  1997 - PECO  announced it was interested in  buying  a  portion  of

the  25-year-old   Main  Yankee  nuclear  power  plant. (Main  Yankee  was  closed  by

its  owners  on  May  27,  1997.  Day-to-day  operations  were  taken  over  by  the

Entergy.)  Earlier,  in  the  year,  PECO  offered  to  purchase  Cajun  Electric  Power

Cooperative’s  30%  stake  in  the  River  Bend (940  MWe)  nuclear  generating

station  for  $50 million.  The  Agreement  with  Cajun  was  approved  by  a  US

Bankruptcy  Court  on May  29,  1997. (Complied  from  articles  in  the  Patriot  News,

June  5  &  23,  1997  and  a  PECO  Press  Release,  June  5,  1997.) (See  September  11

and  October  3,  1997  and  June  17,  1998,  for  related  developments.  Cajun

updates  can  be  found  on  May  27,  1998  and  May  27,  2000).

June  18,  1997  -  A  number  of  environmental  and  consumer  organizations

and Senator Vincent Fumo   filed  separate  appeals to the PUC’s May 22 decision

allowing PECO to  bill  customers $1.1  billion in  “stranded  costs.” (PR  Newswire,

June  18,  1997.)  (See  April  1  &  14  and  May  22,  1997,  for  background  data.)

July  1,  1997 -  Two  high  pressure  service  water  system  motor  operated

valves  failed  to  close.

July  10,  1997 -  Problems  relating  to  the Main  Control  Room  Emergency

Ventilation  radiation  monitor  were  identified  by  the  NRC.  (See  May  15,  1998,

for   additional  issues  and  a  violation  resulting from this  deficiency. Also,  see

September  12,  1997,  for  a  related  problem.)

July  17,  1997  -  During  the  SALP  evaluation,  the  NRC  found  “...there

were  several   instances  where  operating  procedures,  surveillances,  and  tests

were  not  consistent  with  the  design  and  licensing  basis...However,  some  balance

of  plant  equipment  problems  challenged  operators,  indicating  continued

attention to  equipment  performance  is  needed. Also,  we  found  problems  with the

development  and  management   oversight  of  efforts  to  implement  the

maintenance  rule  program.”  (Hubert  J.  Miller,  NRC,  Regional  Administrator,

Jul y   17,   1997. )-  July  24,  1997 -  The  NRC  found:  “...in  one  instance,  an  operator

installing  a  jumper  caused  the  loss  of  high  pressure  coolant  injection  automatic

initiation  capability for  a  short  period  of time.  Our  review  of the  issue found

procedural  guidance  provided to the  operator  was  lacking,  in that,  it  did  not

specify  how to  install the  jumper  or  precautions  on  possible  problems that  could

occur.  Maintenance  personnel  performed,  well...However,  in  one  instance  a

single  control  rod  scrammed  due  to   maintenance  technicians  pulling  the  wrong

fuses  during  electrical  isolation....Your  evaluation  and  control  of  non-routine

effluent/material  release  paths,  such  as  sampling  and  analysis  of  sewage  solids

and  burning  of  slightly  contaminated  oil,  showed  some  weaknesses,  indicating  a

need  for  further  attention  in this  area....Based  on the  results  of this  inspection,

the  NRC  has  determined  that  a  violation  of  NRC  requirements  occurred...This

violation  is  of  concern  because  several  grand  master  keys  were  not  properly

controlled.” (Paul  D.  Swetland,  Acting  Chief,  Projects  Branch  4,  Division  of

Reactor  Projects,  July  24,  1997.)

August  14,  1997  -  “...during  surveillance  testing,  the  diesel  driven  fire

pump  starting  battery  exploded  shortly  after  the  start  of  the  pump.  Operators

immediately  shut  down  the  the  pump  and  notified  supervision...Plant

management  initiated  a  full  root  cause  investigation  for  this  event.  Initial

reviews  by  the  investigation  team  determined  that  on  June  25,  predictive

maintenance  personnel  had  identified  uneven  battery  electrolyte  heating.  Also,

a  separate  action  request  had  identified  higher  than  normal  current  on  the

battery  charger.  maintenance  recognized  that  the  combination  of  high  current

and  uneven  heating  was  an  indication  of  cell  failure;  however,  no  action  was

taken  to  accelerate  the  scheduled  replacement  of  the  battery.  Further

investigation  revealed  that  the  battery  cables  had  a  low  resistance  to  ground  ,

which  could  contribute  to  the  premature  failure  of  the  battery.  The  diesel  driven

pump  uses  stranded  24  Volt  truck  batteries.”  (IR  50-277/97-06  &  50-278/97-

0 6 . )

August  28,  1997 - At  Unit-2,  “operators  experienced trips  of the two

running  drywell  chillers,  resulting  in  a  loss  of  drywell  cooling for  a  period  of

several  minutes.”  (IR  50-277/97-06  &  50-278/97-06.)

August  29  and  30,  1997 - At  Unit-2,  “power  was  reduced to  90% for  work

on  a  condensate  demineralizer.”  (IR  50-277/97-06  &  50-278/97-06.)

September  1997 -  “Earnings  for  the  six  months  ended  June  30,  1997

were  $1.02  per  share  as  compared to  $1.08  per  share for the  corresponding

period  in  1996.” (Report  to  Shareholders,  C.A. McNeill,  Jr.,  Chairman,  and

CEO.)

September  2,  1997 -  At  Unit-2,  “a  fire  occurred  in  the  3B  circulating

water  pump  motor.”  (IR  50-277/97-06  &  50-278/97-06.)  (See  November  6,

1995  and  January  14,  1998  for  related  incidents.)-  September  11,  1997 -  “PECO  Energy  Company (NYSE:  PE),  of

Philadelphia,  and  British  Energy,  of  Edinburgh,  Scotland,  announced  today

formation  of  a  joint  venture,  AmerGen  Energy  Company,  LLC,  to  pursue

opportunities  to  acquire  and  operate  nuclear  generating  plants  in  the  United

States.” (Company  Press  release.) (See  June  5  and  October  3,  1997  and May  27,

July  17,  1998,  June  25,  1999,  and  June  9,  2000,  for  related  developments.)

September  12,  1997 - A  Notice  of Violation  was  issued  dealing  with

PECO’s  “troubleshooting  of  the  main  control  radiation  monitor,  during  which

and  communication  weaknesses  led  to  a  noncompliance  with  technical

specifications...in  a  few  instances,  your  staff  did  not  formally  review  issues  with

potential  for  learning  opportunities.  Examples  included  the  missing  E-2

emergency  diesel  generator  exhaust  gasket,  and  inconsistencies  between  plant

procedures  and  technical  specifications  associated  with  emergency  diesel

generator  starting  air  reservoir  pressure.”  (Clifford  J.  Anderson,  NRC,  Chief

Projects  Branch  4,  Division  of  Reactor  Projects.) (See  July  10,  1997  and May  15,

1998,  for  related  problems.)

September  12,  1997  -At  Unit-2,  “power  was  reduced  to  approximately

60%  power  for  hydraulic  control  unit  maintenance  and  condenser  waterbox

cleaning.”   (See  November  18,  1994;  July  16,  September  10  and  October  25,

1996;  and  ,  September  12,  1997  for  related  incidents.)  (IR  50-277/97-06  &  50-

2 7 8 / 9 7 - 0 6 . )

September  12,  1997 -  At  Unit-2,  “workers  identified  a minor  leak  in the

HPSW  [High  Pressure  Service  Water]  monitoring  system  caused  by  a  slightly

opened  instrument  valve  and  a  missing  threaded  cap.”  (IR  50-277/97-07  &  50-

2 7 8 / 9 7 - 0 6 . )

October 3, 1997 - The  Financial  Times of London identified PECO Energy

Company  as making  a  bid to  purchase Three Mile Island from  GPU Nuclear.  Due

to  a  confidentiality  agreement,  GPUN  would  not  confirm the  name  of the

company  interested  in  purchasing  TMI.  (See  July  5  and  September  11,  1997  and

June  17,  1998  for  related  developments.)

October 8,  1997 -  “Enron Corp. is  seeking to takeover PECO Energy Co.’s

Pennsylvania  service  area,  offering  to  lower  customers’  electric  rates  by  20

percent  and  assume $5.5  billion  in Peco  costs.” Patriot  News, October 8,  1997.

(See November  28,  2001,  for  a  related  development.)-  October  15,  1997 -  “We  noted  during this  period two  examples  where

personnel  either failed to follow procedures  or failed to take  adequate  selfchecking measures,  resulting  in  one  case  in the  conduct  of  a  surveillance test  on

the  wrong  unit. Moreover, two  days  after this  inspection  period  ended,  your  staff

identified  an  event  inn  which  a  safety-related  high  pressure  service  water

(HPSW)  pump  was  electrically  uncoupled  without  being  isolated  because

contractor  personnel  thought  they  were  working  on  a  non-safety-related  service

water  pump  that  was  electrically  isolated.  This  event  highlighted  weaknesses  in

procedural  adherence,  particularly  in  the  use  of  work  package  documentation  at

the  job  site,  self-checking,  and  a  questioning  attitude that  led to multiple

breaches  in  work  process  barriers.

“The  HPSW  event  is  of  particular  concern  since  it  impacted  a  safetyrelated  piece  of  equipment.  It  also  represented the third  significant

industrial  safety  event  since late  February  at  Peach  Bottom, (bold faced

added), the  other two being the unexpected  start  of  a  cooling tower fan while  a

worker  was  preparing to take  an  oil  sample from the fan  gear  box,  and the

injection  of  chlorinated  water  into  a  circulating  bay  while  two  workers  were

conducting  a  pump  inspection. (See  December  16,  1997  for  a  related  HPSW

incident.)   Management’s  attention  to  effectively  correcting  the  work  clearance

process  and  worker  performance  weaknesses  noted  in these  events  is  warranted,

particularly  given  the  increase  in  the  number  of  work  activities  and  contract

workers  during the  Unit  3  outage.” (NRC,  Clifford  J. Anderson,  Chief  Projects

Branch  4,  Division  of  Reactor  Projects.)

October  15,  1997 -  “A  discovery  of  a  licensee  operating their  facility  in  a

manner  contrary  to  the  Updated  Final  Safety  Analysis  Report  (UFSAR)

description  highlighted  the  need  for  a  special  focused  review  that  compares  plant

practices,  procedures  and/or  parameters  to  the  UFSAR.  description. While

performing  the  inspections  discussed  this  report,  the  inspector  reviewed  the

application  portions  of the UFSAR that  related to  areas inspected. The inspector

verified  that  the  UFSAR  wording  was  consistent  with  the  observed  plant

practices,  procedure  and/or  parameters.  (IR  50-277/97-06  &  50-278/97-06.)

October 20,  1997 - The potential for the  suppression pool to be bypassed

during  a  loss-of-coolant-accident  at Unit-1  & Unit-2 was  identified. PECO

identified  this  event  (#33121)  as  an  “outside  design  basis”  incident.  (See  August,

1999,  for  more  information.

October  29,  1997 -  At  Unit  3,  PECO  identified  a temperature  differential

of  84  degrees  F.  “RPV [Reactor  Pressure Vessel]  coolant temperature  was  163

degrees  F  with the  ‘B’  recirculation  loop temperature  at  79  degrees  F. (IR  50-

277/98-06;  50-278/98-06;  NOV.)  (See  March  23,  1998,  for  related  problems

and  a Notice  of Violation.)-  November  1,  1997 -  A  failure  to  trip  at  Unit-2  involving  the  Reactor

Feedwater  Pump  Turbine,   “was  originally  attributed  to  intermittent

mechanical  binding  of  some  trip  mechanism  sub  components.”  (IR  50-277/98-

03;  50-278/98-03.)

(See  April  1,  1997,  for  a  related  incident.)

November  7,  1997 -  “PECO  Energy  of  Philadelphia  had  the  highest

number  of  justified  consumer  complaints  in  1996  among  electric  utilities,  as

well  as the  longest  response time to those  complaints [Pennsylvania  Public

Utility  Commission].”  (Patriot  News,  November  7,  1997,  B7.)

November  9,  1997 -  The  unit  2  reactor  scrammed. (See  December  6,

1997,  for  root  causes  of  scram.)

November  28,  1997 - Unit  3  was  shut  down to  replace the  ‘E’  steam  relief

v a l v e .

December  1997 -  “Earnings  for the  nine months  ended  September  30,

1997  were  $1.71  per  share  as  compared  to  $1.73  per  share  for  the  corresponding

period  in  1996.”  (PECO  Energy, Report  to  Shareholders,  Third  Quarter  1997,

C.A.  McNeill,  Jr.,  Chairman,  President  and  CEO.)

December  16,  1997 -  Following  an NRC  inspection, the  staff  reported,

“...the  practice  of  permitting  blanket  approvals  for  overtime  work  on  safetyrelated  activities  for  multiple  weeks  with  no  hourly  limit  specified  resulted  in

abuses  that  were  considered  a  breach  in  the  intent  of  the  overtime  authorization

process.” (02.3) (Executive  Summary.)

Although  the  Agreement  between  PECO  and  the  Commonwealth  expired

in  1993,  Section  5.4  established  “restrictions  on the  use  of  overtime  for  plant

personnel  who  perform  safety-related  functions.”  (June  1989.)

December  16,  1997 -  During  an  NRC  inspection, the  staff  observed:  “...

findings  by  your  staff  late  in  the  Unit-3  refueling  outage  regarding  the  existence

of  cracking  of three  of the ten  recirculation  riser pump  elbow welds posed  a

noteworthy  challenge  to  your  engineering  organization  and  resulted  in  the

development  of  a  plant  operating  strategy  that  limited  recirculation  flow  until  a

mid  cycle  outage  can  be  performed  in  1998.

Continued on the following page...“Multiple  examples  of  a  violation  of  NRC  requirements  were  identified

during this  period.  Specifically, three  examples  of  a  failure to  follow  procedures

were  identified, two  in the  Operations  area  and  one  in the Maintenance  area. We

are  concerned  with  these  examples  of  procedure  non-adherence  given  their

impact  on  plant  equipment  and  their  potential  industrial  safety  implications

(i.e.,  one  which  directly  caused  a  Unit  2  reactor  scram  [November  9,  1997  at

100%  power]  and  another  which  significantly  contributed  to  maintenance

personnel  inadvertently  rendering   a  safety-related  HPSW  [high  pressure  service

water]  pump  inoperable  [September  22,  1997]  without  it  being  electrically

isolated  during the  conduct  of  work.) (See  October  15,  1997 for  a  related HPSW

e v e n t . )

“This  violation is  cited in detail in the  enclosed Notice  of Violation  and the

circumstances  are  described  in  detail  in the  enclosed  inspection  report.” (NRC,

Clifford  J. Anderson, Chief,  Projects Branch  4,  Division  of  Reactor  Projects.)

December  23,  1997 -   “...Unit  2  was  shut  down to  replace the  secondary

pressure  amplifier  card  and the  potentiometer  assemblies  on the  pressure  control

unit  fro  the  ‘B’  EHC  [electro-hydraulic  control]  regulator.”  (IR  50-277/97-08  &

50-278/97-08.)  (See  December  29,  1997  for  a  related  incident.)

December  23,  1997 -  “...plant  management  chose  to  shut  down  Unit  2

due  to  problems  with  the  pressure  regulator  control  circuit.  On  December  15,  the

back  up  EHC [electro-hydraulic  control]  pressure  regulator  ‘B’ took  control  of

reactor  pressure  without  operator  action.”  (IR  50-277/97-08  &  50-278/97-08.)

-  December  29,  1997  -  “...all  nine  bypass  valves  unexpectedly  opened  at

155  psig  EHC  [electro-hydraulic  control]  pressure  during  the  normal

depressurization/cool  down  of  Unit  2.  Operations  and  engineering  personnel

failed to  understand the  effect  of the EHC  system  of  a temporary  plant

alteration...This  lack  of  system  understanding  contributed  to  all  bypass  valves

unexpectedly  opening  which  resulted  in  a  reactor  vessel  level  transient.”   (IR  50-

277/97-08  &  50-278/97-08.)

December  29,  1997 -  “...Unit  2  was  shut  down to  replace  amplifier  card

and  potentiometer  assemblies.”  (IR  50-278/97-08;  50-277/97-08.)  (See

December  23,  1997  for  a  related  incident.)-  January  1,  1998 -  “...  the  Unit  2 main  turbine  tripped  on main  oil  pump

low  pressure  during  plant  start-up  after the turbine  rolled to  a  speed  of  1400

RPM.  Operations  personnel  were  unaware that the turbine  had  been  rolling  for

over two hours just prior to the trip. This issue  appeared to involve  a failure  of  an

instrument  and  control  test  document  to  restore  the  original  [electro-hydraulic

control]   EHC  [electro-hydraulic  control]  system  alignment  after  testing  and  the

failure  of  operations  personnel to fully follow  procedures. Concerns were  also

identified  with the  pulling  of  control  rods to  increase  reactor  pressure  during this

event  and failure  of  operations  personnel to  recognize  status  of the main turbine

or  turbine  control  systems.”  (IR  50-277/97-08  &  50-278/97-08.)

“Several  examples  of  weak  control  room  oversight  of  activities  were  noted

from  the  Unit  2  main  turbine  trip  during  start-up  on  January  1,  1998...1)  The

Control  Room  Supervisor  directed the  pulling  of  control  rods to  increase  reactor

coolant  system  pressure  while  the  turbine  condition  remained  known.  2)  Shift

turnover  and  the  shift  meeting  occurred  while  the  turbine  was  in  this  unknown

condition  even though members  of the  crew  knew that the turbine  had  come  off

of  the  turning  gear.  3)  The  crew  with  the  watch  during most  of  this  event  had

not  received  any  just-in  -time  training  such  as  simulator  runs  even  though  this

was the first  reactor  start-up for the  Plant  Reactor  Operator  and the Control

Room  Supervisor.”  (IR  50-277/98-01,  50-278/98-01.)

January  2,  1998 -  “... the  unit  2  reactor  operator  failed to  perform the

technical  specification  (TS)  surveillance  requirements  (SR)  for  verification  of

proper flow  in the  recirculation  loops. The  recirculation  loops  were  not  operated

outside  of the  TS  requirements  during this  period.  However,  it  was  unclear  how

station  personnel  determined the formal  TR  SRs  were met  and  why  operations

personnel  failed to  review the  TSs  when  unclear  information  was  found  in the

surveillance  test.”  (IR  50-277/97-08  &  50-278/97-08.)  These  actions  violated

SR  requirements.

- January  2,  1998 -  Operations  personnel failed to take  or  record the

readings  for  the  Surveillance  Test  for  “Daily  Jet  Pump  Operability.”

January  3,  1998  -  “...operations  personnel  discovered  that  the  Unit  2

reactor  operator (RO)  failed to  perform the technical  specification (TS)

surveillance  requirement  for  verification  of  proper  flow  in  the  recirculation  loops

following  start-up”   (IR  50-277/99-01;  50-278/99-01.)-  January  4,  1998  -  “...the  main  steam  line  bypass,  BPV-1,  unexpectedly

opened  approximately  25%  several  times  while  the  Unit  2  reactor  was  raising

reactor  power  from  96%  to  100%. Instrument  and  control  room  technicians

unknowingly introduced  sped  error  bias in the  speed  control portion  of the EHC

[electro-hydraulic  control]  system  after  they  tightened  a  loose  connection  during

replacement  activities  for  the  EHC  pressure  control  unit.  Instrument  and  control

personnel  failed to  understand  what  effect tightening the  loose  connection  on the

speed  control would have on the  speed bias  signal and EHC  system.”   (IR 50-

277/97-08  &  50-278/97-08.)

- January  5,  1998 -  “...during  maintenance  on  the  2  ‘C’  RHR  heat

exchanger,  technicians  found  broken  glass,  an  electrical  extension  cord,  and

metal  straps  on the  RHR (shell)  side  of the  heat  exchanger.  Technicians  removed

the  glass  but  were  unable to  remove the  cord  and metal  straps.

After  further  investigation,  PECO  determined  that  the  foreign  material

had  been  previously  identified  in  the  heat  exchanger  in  1994.”  (IR  50-277/97-

08  &  50-278/97-08.)

January  5,  1998 -  “Illinois  Power  said Monday  it  contracted  an  outside

nuclear  team  from  PECO  Energy  Co  to manage  its  Clinton  Power  Station,  which

has  been  shut  down  since  September  1996...Clinton  is  a  950-megawatt  boiling

water  reactor. Water McFarland,  vice  president  of  PECO’s  Limerick  Station,  is

Illinois Power’s new  chief  nuclear  officer. He  assumes  responsibilities

immediately.”  (R e u t e r s,  January  5,  1998.)

“Under  the  three-year  contract,  which  may  be  renewed  for  an  additional

five  years,  a  core  group  of  PECO  Nuclear  employees  will  provide  management

expertise  to  Illinois  Power.”  (PECO  Energy,  1997  Annual  Report,  February  2,

1998,  p.  4.)

January  12,  1998  -  “While  transferring  a  contaminated  filter  from  the

spent  fuel  pool  to  a  shipping  cask  on  January  12,  1998,  an  area  radiation

monitor (ARM)  alarmed  at  20  millirem  per  hour.  Personnel  working  in  the  area

moved to  lower  dose  areas  with the  exception  of the  radiation technician  and the

overhead  crane  operator  on  the  bridge.  The  radiation  technician  was  monitoring

radiation  levels  and  informed  the  operator  levels  had  not  significantly  changed.”

(IR  50-277/99-01,  50-278/99-01.)

January  14,  1998 -  At  Unit  2,  “power  was  reduced  to  97%  when

condenser  vacuum  decreased  after  the  2  ‘C’  circulating  water  pump  failed  to

start  and  the  pump  discharge  valve  failed  [to]  open  during  post-maintenance

testing.”  (50-277/97-08  &  50-278/97-08.)  (See  November  6,  1995  and

September  2,  1997,  for  related  incidents.)-  January  28,  1998  -  “The  practice  of  the  control  room  supervisor  leaving

the main  control  room  work  station  for  brief  periods  without temporary  relief

from  another  senior  reactor  operator  demonstrated  weak  oversight  of  control

room  activities.

“On  January  28,  1998,  the  control  room  supervisor  left  the  main  control

room  work  station  without  temporary  relief  for  several  minutes  to  verify

acknowledgment  of  an  expected  alarm.”  The  NRC  identified  a  violation  of

technical  specifications.  (IR  50-277/98-01,  50-278/98-01.)

“...the  NRC  identified  that  a  control  room  supervisor  did  not  visually

verify  or  verbally  communicate  alarm  acknowledgment  of  an  expected  alarm

that  came in  on Unit  3  because  he was  outside  his  designated work  station

without  temporary  relief.”

(Severity  Level  IV  violation,  IR  NOS.  50-277/98-01  AND  50-278/98-01.)

January  29,  1998  -  “On  January  26,  1998,  PECO  Energy’s  Board  of

Directors  voted  to  reduce  the  Company’s  quarterly  common  stock  dividend  from

45  cents  per  share to  25  cents  per  share,  effective  with the  first  quarter  dividend,

payable  on  March  31,  1998  to  shareholders  of  record  on  February  20,  1998.  This

is  a  result  of the  Pennsylvania Public  Utility Commission (PUC)  orders  issued  in

December  and  January...

January  30-31,  1998 -  “...operators  reduced  power  to  about  93%  to  allow

for  repairs  of  the  2C  circulating  pump  discharge  valve.”  (IR  50-277/98-01,  50-

2 7 8 / 9 8 - 0 1 . )

February  6,  1998 - At Unit  2,  “power was  reduced to  about  90% to

investigate  trip  problems  with  the  2A  reactor  feed  pump  turbine.” (IR  50-

2 7 7 / 9 8 - 0 1 ,   5 0 - 2 7 8 / 9 8 - 0 1 . )

February  13,  1998 -   “Unit  3  began the  period  operating  at  94%  power.

This  unit  was  operating  at  less than  full  power  due to  recirculation  system  flow

rate  limitations  because  of  weld  cracks  on the  jet  pump  risers.  On  February  13,

power  was  increased to  100%,  as  allowed  by the  operating  strategy  for the  jet

pump  riser  cracks.”  (See  March  6,  1998  for  follow-up  incident.)  (IR  50-277/98-

01 ,   50-278/98-01 . )

March,  1998 -  “The Company  reported  a  net  loss for  1997  of $1.5  billion

or  $6.80  per  share. Included  in  these  results  was  an  extraordinary  charge  of  $3.1

billion ($1.8  billion  net  of taxes),  or  $8.24  per  share,  in the fourth  quarter to

reflect  the  effects  of  the  December  1997  PUC  order (as  revised  in  January  1998)

in  the  Company’s  restructuring  proceeding.”  (Report  to  Shareholders, C.A.

McNeill,  Jr.,  Chairman,  President  and  CEO,  PECO  Energy.)- March  1998 -  “PECO  personnel  identified that five Fire Areas  in the

plant,  containing  25  rooms,  did  not  contain  automatic  fire  detection

systems...PECO  intends  to  submit  an  exemption  request...for  the  identified  Fire

Areas.”  (IR  50-277/98-10,  50-278/98-10;  NOV.)

- March  6,  1998 - Power  at Unit  3 was  reduced to  94%.

March  11,  1998 -  PECO  Energy  Company  announced  it  was  counter

suing  Great  Bay  Power  Corporation  “to  prevent  it  from  ending  a  power

marke t ing  agr e ement .

“PECO,  which  is  seeking more than five million  in  damages for  breach  of

contract  and for the loss  of  goodwill  and harm to its  reputation, filed the  suit in

the  U.S.  District  Court  of  New  Hampshire.

“This  suit  comes  a  week  after  Great Bay  sought to  end the  exclusive

marketing  agreement  to  sell  Great  Bay  power  generated  at  the  Seabrook  1

Nuclear  Power  Plant  in  Seabrook,  N.H. [Great  Bay  owns  12.1%  of  Seabrook.]

“Great Bay  also  sued PECO  last  week for  breach  of  contract,  charging PECO

entered  into  a  number  of  wholesale  agreements  in  its  own  name  without  telling

Great Bay  or  submitting bids  on behalf  of Great Bay  and that PECO  ‘failed to  offer

Great  Bay’s  power  to  customers  as  required  under  the  marketing  agreement’  ”

(Re u t e r s,  March  11,  6:07  Eastern  Time.)

June  3,  1998-  Great  Bay  Power  Corporation  withdrew  its  lawsuit

against  PECO.     John  A.  Tillinghast,  Great  Bay’s  Chairman  said,  “We  believe

PECO  acted  properly  as  our marketing  agent.  And  seems  clear that the  judge  in

our  case is inclined to find that PECO did not  breach the marketing

agreement....PECO’s  acceptance  of  our  proposal  lets  us  get  started  on  our  own

marketing  strategy.  We  appreciate  the  value  PECO  has  provide  Great  Bay  over

the  past two  years  and  wish them  well  in the  future.” (PECO  Energy,  Press

Release,  June  3,  1998.)

March  13,  1998 -  Unit  3  was  “shutdown  for  outage  3J12, to  perform

repairs  to  the  jet  pump  risers.”  (Set  February  13,  1998  for  related  information.)

(IR  50-277/98-01,  50-278/98-01.)

March  21,  1998 - At  Unit-2,  “unit  load  was  reduced to  perform  control  rod

pattern  adjustments,  waterbox  cleaning,  and  reactor  feed  pump  turbine

testing.”  (IR  50-277/98-02; 50-278/98-02.)

March  22,  1998 -  The  NRC  noted  “reactor  engineers  did  not  recommend

positive  actions  to  reduce  a  thermal  limit  ratio  when  approaching  the  Technical

Specifications  limit,  which  did  not  meet  operations  department  expectations  for

conservative  plant  operations.”   (IR  50-277/98-02;  50-278/98-02.)- March  23,  1998 -  PECO  “identified that they  failed to  properly

implement  the  improved  Technical  Specification  Surveillance  Requirement

3.4.9.4  for  the  start  of  the  first  recirculation  pump.  Between  January  18,  1996,

and  March  23,  1998,  operations  personnel  were  not  verifying  that  the

temperature  differential  between  the  reactor  coolant  in  the  recirculation  loop

being  started  and the  reactor  pressure  vessel  coolant  was  within  50  degrees  F.

On  October  27,  1997,  the  ‘B’  recirculation  pump  was  started  with  a  differential

of 84 degrees F. Although this did not  exceed design limits nor impact fuel

performance,  it  was  a  violation  of  Technical  Specification  Surveillance

Requirement  3.4.9.4.  (Section  08.1).  (IR  50-277/98-06;  50-278/98-06;  NOV.)

(See  October  29,  1997,  for  a  precursor  event.)

March  25,  1998 - At  Unit-3,  “foreign material  was found  in the  3A  core

spray  pump.  (IR  50-277/98-02; 50-278/98-02.)   (See  May  1,  1998  regarding  a

violation  related  to  this  event. (Also,  see  December  11,  1998,  for  a  related

i n c i d e n t . )

- March 25,  1998 - A Notice of Violation was issued for  cold weather

preparations’  procedural  noncompliances.  (IR  50-277/98-11,  50-278/98-11).

March  30,  1998  -  “...violations  of  NRC  requirements  occurred,  namely,

(1) the  failure to  perform  certain  required tests; and (2) the  creation  of

inaccurate  records  to  indicate  that  the  tests  were  performed.”  Charles W.  Hehl,

NRC,  Director,  Division  of  Reactor  Projects.)

“...  inspectors  noted that the  control  room  staff  was  not  aware that

maintenance  personnel  were  performing  post-maintenance  test  cycling  of

vacuum  relief  valve...during  the  drywell  walkdown.  Communications  between

maintenance  and  control  room  personnel  were  not  effective...

“...  inspectors  noted  increased  noise  in the  control  room  during  peak

activity  periods.  During these  periods, there  were  15 to  20  people  in the  control

room.  During these  periods  order  in the  control  room  was  challenged.  During

periods  with  fewer  personnel  in the  control  room  and  decreased  activity, the

inspectors  observed that  operation  of the  unit  became more  deliberate.” (IR  50-

277/98-02;   50-278/98-02. )- March 30,  1998 - A  violation was  recorded by the NRC form PECO’s

failure  “during  several  months  to  maintain  the  2’  A’  Reactor  Feedwater  Pump

Turbine  High Water  Level  Trip  function  operable  as  required  by  Technical

Specification...We  concluded  during  this  inspection  that  your  corrective  actions

for the  first two  failures  were  not  comprehensive.  There  were  a  number  of

previous  opportunities to  identify  and  correct the  root  cause  of these  events

particularly  through  at-power  verification  testing.  Also,  we  noted  that  the  2’  A’

feedwater  system  change  of  status  maintenance  to  a  maintenance  rule  (a)  1

system  was  not  timely.  Although  this  change  met  your  administrative

requirements,  we  viewed  the  status  change  as  untimely  based  on  the  technical

specification  significance.” (Charles W.  Hehl,  NRC,  Director,  Division  of  Reactor

Projects.)

April  16,  1998 - The NRC  “observed that the  Unit  2’ B’  stream  jet  air

ejector  main  steam  supply  header  control  room  valve...was  not  in  its  expected

position...This  item  remains  unresolved  pending  further  progress  in  these

investigations...”   (IR  50-277/98-02;  50-278/98-02.)

April  27,  1998 - At  Unit-2,  “unit  load  was  reduced  due to  an  inoperable

control  rod.”  (IR  50-277/98-02; 50-278/98-02.)

April  28,  1998 -  “The  3A  stator  water  cooling  pump  tripped  during

system troubleshooting  efforts  on April  28,  1998,  due to  weaknesses  both  in

operations  review  of  the  work  and  with  communications  regarding  restrictions

on  work  scope.”  (IR  50-277/98-06;  50-278/98-06;  NOV.)

May  1,  1998 -  “We  identified  five  violations  of  NRC  requirements  during

this  inspection.  The  first  violation  involved the  failure  of  a  control  room

supervisor  to  verify  that  a  Unit  3  expected  alarm  was  acknowledged  due  to  the

fact that  he  was  outside  of  his main  control  room  work  station  without

temporary  relief.

“The  next two  violations  were the  result  of  operations  personnel failing to

perform  technical  specification  surveillance  requirements  for  the  verification  of

proper  recirculation  loop  flow  during  Unit-2  start-up  on  January  2,  1998.

“The  fourth  violation  contained  several  examples  of  inadequate  procedures

and  control  room  operators  failing  to  implement  operations  procedures  which

resulted  in  the  unexpected  trip  of  the  Unit  2  main  turbine  on  January  1,  1998.

The  procedures  were  inadequate  since they  failed to  restore the  ElectroHydraulic  Control  system  to  the  alignment  requirement  for  reactor  start-up.

Also,  operations  personnel  failed  to  adequately  implement  procedures  when  they

did  not  recognize the  abnormal main turbine  status,  position  of the turbine

control  valves, or the  selection of the  speed  set for the EHC  system for  several

shifts  prior  to  the  main  turbine  trip.“We  were  concerned  with  the  violations  described  above,  especially  the

Unit  2 main  turbine  trip,  because  they  all  showed  weak  oversight  of  the  control

room  activities.  We  previously  documented  in  Inspection  Report  50-277

(278)/97-07  where  inadequate  oversight  of  operator  activities  contributed  to  a

scram  of  the  Unit  2  reactor  during  swapping  of  a  station  battery  charger.

“The  last  violation  resulted  from  Unit  3  exceeding  the  licensed  power  level

up  to  0.6%  between  October  22,  1995  and  January   21,  1997.  PECO  Energy

Company  operated the  reactor  at  a  steady  state  power  level  up to  100.6%  of

rated  power. We  were  concerned that  your  staff failed to  recognize  errors  in the

calibration  of  feedwater  temperature  instruments  even  after  deficiencies  were

identified  with  the  equipment  used  to  calibrate  these  instruments.  The

inaccurate  feedwater  temperature  instruments  resulted  in  power  levels  above

the  licensed  limit for  over  15 months.” (NRC, Clifford  J. Anderson, Chief,  Projects

Branch  4,  Division  of  Reactor  Projects.)

Two  “apparent  violations”  were  identified  during  a  special  NRC  inspection

r e p o r t .

“These  violations  resulted  from:  1)  the  failure  to  prescribe  and  accomplish

the  ECCS  [emergency  core  cooling  system]  strainer  replacement  modification

with  documented  instructions  and  procedures  appropriate  to  the  circumstances

to  prevent  the  introduction  of  foreign  materials  into  the  core  spray  system,  and

2) the  failure to maintain the  3A  core  spray  pump  operable  as  required...”   [See

March  25,  1998,  for  information  on  the  3A  core  spray  incident.]  (NRC,  Charles

W. Hehl, Director, Division of Reactor Projects.)

May  5,  1998 -  “...during  testing,  operators  observed  candle-sized  flames

on  the  E2  EDG  exhaust  manifold.”  (IR  50-277/98-06;  50-278/98-06;  NOV.)

(See  June  9,  1998,  for  a  related  incident.)

May  12,  1998 - At  Unit  2,  “unit  load  was  reduced to  withdraw  a  control

rod following  repairs to  one  its  scram  solenoid  pilot  valves.” (IR  50-277/98-06;

50-278/98-06;  NOV.)  (See  June  1,  1998,  for  a  related  incident,  and  March  22,

2000,  for  a  similar  challenge).

May  14,  1998 -  “Four  licensed  operators missed training  for the two  year

requalification  period  that  ended  in March  1996  and  never  made  up  the  missed

training  within  a  reasonable  time  thereafter.  This  was  unresolved  pending  NRC

staff  review for  enforcement  action  with  respect to  10 CFR  55.59  a (1). (IR  50-

277/98-04;  50-278/98-04  and  NOV.)- May  14,  1998 -  The  NRC  identified two  violations  relating to  licensee

operator  requalification  training  (LORT).   “The  first  violation  involved  a  failure

to  assure  sufficient  differences in the job  performance measure (JPM)  portion  of

the  operating test  administered to  different  crews  on  different  weeks.  This

violation  is  of  concern  because  of the  potential for  precluding the  identification  of

retraining  needs.  The  second  violation  involves  the  failure  of  your  operating  test

to  evaluate  SROs [senior  reactor  operators] fulfilling the  role  of the  control  room

supervisor  in  their  ability  to  execute  the  emergency  plan.  This  violation  is  of

concern  since the SROs may be  called upon to  execute the plan in the  absence of

shift  managers.”  (IR  50-277/98-04;  50-278/98-04.)

May  14,  1998 - The  NRC  identified  a  violation  “for failure to  include the

area  of  radiation  monitoring  system  within  scope  of  the  maintenance  rule

program...This  violation  is  of  concern  since  scoping  problems  of this type  have

been  identified  through  recent  operating  experience  and  findings  from  NRC

maintenance  rule  baseline  inspections  and  the  violation  represents  an  apparent

failure  to  incorporate  this  information  into  your  program.”  (IR  50-277/98-04;

50-278/98-04;  and  NOV.)

May  15,  1998 -  “...operations  personnel  identified  that  the  trip  relay  for

the  Main  Control  Room  Emergency  Ventilation  (MCREV)  radiation  monitor  had

not  been  in the tripped  status  for  approximately  28  hours  while the  ‘B’  channel

radiation  monitor  was  inoperable.”  This  was  a  violation  of  the  technical

specifications.

“The  operations  personnel  installing the  jumper to  initiate  a  Division II

isolation trip of the MCREV  radiation monitor did not perform, nor did the

procedure  instruction  require,  a  positive  verification  that  the  trip  was  properly

inserted.  The  corrective  actions  from  the  July  10,  1997  event  were  not

comprehensive  enough  to  prevent  the  subsequent  event.  (Section  02.1).  (IR  50-

277/98-06;  50-278;  98-06;  NOV.)  (Also  see  September  12,  1997;  June  7  &  July

17,  1998  for  related  problems.)

May  16,  1998 -  “During  a  Unit  2  power  down  evolution  on May  16,

1998,  operators  reduced  speed  on  an  incorrect  reactor  feed  pump,  resulting  in  a

reactor  level  excursion  and  recirculation  system  runback.  The  event  was

indicative  of  poor  operator  performance,  reflecting  weaknesses  in

communications,  self-checking,  and  peer/supervisory  review.”  (IR  50-277/98-

06;  50-278/98-06;  NOV.)  (See  related  incidents  on  March  17,  199;,  March  4,

1996;  June  7  and  July  13,   1998.)   - May  19,  1998 -  The  NRC  issued  a  “confirmatory  order modifying  the

license  of Peach Bottom  Units No.  2  and No.  3  requiring that the Company

complete  final  implementation  of  corrective  actions  on  the  Thermo-Lag  330

issue  by  completion  of the  October  1999  refueling  of Peach Bottom Unit No.  3”.

(PECO  Energy  Company,  Form-10/K-A,  p.  10).   (See  September  12,  1994,

October  1,  1996,  October  12,  1999,  and  July  21,  2000,  for  background

i n f o rma t i o n . )

May  22,  1998 - Unit  power  was  reduced  at Unit  2 for  condenser  waterbox

c l e a n i n g .

May  27,  1998 -  “The  U.S.  Justice  Department  on Wednesday  said  it  sued

Philadelphia-based PECO Energy Co (PE - news) for more than $67 million in

damages  because  the  company  allegedly  reneged  on  an  agreement  to  buy  a

share [30%  interest  in  the  River  Bend  nuclear  power  plant  owned  by  Cajun

Electric  Power  Cooperative, Inc.]  of  a  Louisiana  nuclear  power  plant.” (Reut e r s,

Wednesday  May  27,  1998,  7:55  pm,  Eastern  Time.)  (See  June  5,  September  11,

and  October  3,  1997  and  May  27  and  June  17,  1998  for  background

information  and  related  developments).  (Cajun  update  can  be  found  on  May  27,

2 0 0 0 ) .

May  29,  1998 - At Unit  3,  “unit  load  was  reduced to  clean  condenser

water  boxes.”  (IR  50-277/98-06; 50-278/98-06; NOV.)

June  1,  1998 - At Unit  2,  “unit load was  reduced following  a  scram  of  a

control  rod  during  reactor  protection  system testing.  The  control  rod  had  a

leaking  scram  solenoid  pilot  valve. The  unit  power  was  reduced  on  June  5 to

facilitate  control  rod  hydraulic  control  unit  (HCU)  on-line  maintenance  to

replace  several  scram  solenoid  pilot  valves.”  (IR  50-277/98-06;  50-278/98-06;

NOV.)  (See  May  12,  1998,  for  a  precursor  event.)

June  7,  1998 -  “...the  3A  recirculation  pump  ran  back to  30%  speed  due

to the unexpected loss  of   a  500  kv line during  an  electrical  storm  and the  slow

opening  of the  500  kv  breaker.  The  3B  recirculation  pump  remained  at  full  speed

during this  event. Due to the difference in pump  speeds  of the Unit  3 pumps, the

flows  in  the  recirculation  loops  were  significantly  mismatched.  The  recirculation

loop  flows  remained  mismatched  outside  of   Technical  Specification  Surveillance

Requirement  (SR)  3.4.1.1  for  over  12  hours.”  This  was  a  another  violation  of

Technical  Specifications.   (IR  50-277/98-06; 50-278/98-06; NOV.)  (See  May  16

and  July  13,  1998,  for   related  incidents.)

Continued on the following page...“Engineering  personnel  failed  to  recognize  the  potential  for  high  vibration

stresses  on the  ‘A’ jet  pump  loops  due to the  large  recirculation flow mismatch

following  the  3A  recirculation  pump  runback  on  June  7,  1998.  The  potential  for

recirculation  flow  mismatch  to  cause  excessive  vibration  of  the  jet  pumps  and

the jet pump  riser braces was described in the Peach Bottom Design Basis

Document (DBD)   for the  recirculation  system.  This  lack  of  understanding  of the

effects  of this mismatch   contributed to the failure  of  engineering  personnel to

provide  the  necessary  technical  information  to  operations  personnel...

“ Also,  Unit  3  experienced  a  runback  of the  3A  pump  in  December  1993

due to the loss  of power to the  same  relay that dropped  out during this  event.

Part  of the  corrective  action  for this  event  was to  install  a modification  which

would  provide  a  non-interruptible  power  supply  to  the  recirculation  pump

runback  relays.  This  corrective  action,  which  could  have  prevented  the  3A

runback  on  June  7,  was  never  performed.  (Section  E1.1).  (IR  50-277/98-06; 50-

278/98-06;  NOV.)  (Also,  see  March  17,  1995  and  March  4,  1996  for  related

e v e n t s . )

June  8,  1998 -  “... the  3  start-up transfer  became  inoperable  following  a

severe  electrical  storm,  but  this  was  not  recognized  by  operators  until  June  22,

1998.  On  June  15,  the  inoperable  3  start-up  transformer  was  aligned  to  the  2

start-up  and  emergency  source for  over  nine  hours to  support  off-site

maintenance  work.”  The  NRC  “treated”  this  event  as  a  Non-Cited  Violation.

(IR  50-277/98-07,  50-278/98-07.)

An  LER (96-005)  issued  on May  7,  1996,  identified  a  similar  problem.

June  9,  1998 -  The  NRC  identified two  violations  during  an  inspection.

“The  first  violation  involved  a  high  pressure  coolant  injection (HPCI)

system  operating  procedure [discovered  by  the  NRC  on March  22,  1998]   that

did  not  provide  adequate  instructions  regrading  the  HPCI  pump  turbine

vibration  monitoring  system.  The  second  violation  was  the  failure  of   health

physics  personnel to  follow  radiation  area  control  procedures  regrading  posting  of

an  open  door  to  a  potentially  high  radiation  area.

“We  are  also  concerned  about  a  number  of  instances  of  plant  valves  being

identified  out  of their  required  or  expected  position. Although  several  of these

valves  were  in  non-safety  related  systems,  three  valves  were  in  safety  related

systems.  We  determined  that,  taken  collectively,  these  items  represented  a

weakness  in  plant  status  control.” (Clifford  J.  Anderson,  Chief,  Projects  Branch  4,

NRC, Division  of  Reactor Projects.)-  June  9,  1998 -  “...plant  personnel  and the  inspectors  observed  smoking

and  small flames  on the E1 EDG  exhaust manifold flanges,  and the  oil

occasionally   flashed  and  self-extinguished  as  the  temperature  of  the  exhaust

manifold  increased  during  EDG  loading.  The  smoking  and  leakage  essentially

stopped  several minutes  after the  EDGs  were  fully  loaded.” (See May  5,  1998,  for

a  precursor  event.)

“Some  emergency  diesel  generator (EDG)  oil  leak  reduction  strategies  were

not  well-implemented  or  well-communicated  to  operations  personnel.  These

factors  contributed to oil leaks  and flames observed on the E2  and E1 EDG

exhaust  manifolds  in  May  and  June,  1998,  respectively.”  (IR  50-277/98-06;  50-

278/98-06;  NOV.)

- June 12, 1998 - The NRC proposed a  $55,000 fine for PECO for two

program  deficiencies  that  led  to  the  impaired  performance  of  a  Unit  3  emergency

cooling  pump...The  violations  were  identified  during  NRC  inspections  conducted

between  February  12  and March  3  and  from March  30  to  April  24

[1998]...Specifically,  the  violations  stem  from  problems  that  affected  a  Unit  3

core  spray  pump.  The  component  is  part  of the  unit’s  core  spray  system,  which

would be used to keep the  reactor  core  covered and  cooled during a loss-of-coolant

accident.” US NRC, Office of Public Affairs, Region I, King of Prussia, PA, June  12,

1998.)     Continued on the following page...

(For more detailed information on these problems,  see NOTICE OF VIOLATION

AND PROPOSED IMPOSITION OF CIVIL PENALTY - $55,000, June 11, 1998,

NRC  INSPECTION  REPORT  NOS.  50-277/98-03  &  50-278/98-06.)

June  22,  1998  -  “...a  reactor  building  equipment  operator  discovered

during  routine  operator  rounds  that  the  Unit-3  reactor  core  isolation  cooling

system  mechanical  over  speed  trip  tappet  was  not  fully  reset.  Station  personnel

determined  that  the  reactor  core  isolation  cooling  system  had  been  inoperable

since May  4,  1998  which  was the  last time the  over  speed trip  function  was

manipulated  and  successfully  tested.”  (IR  50-277/98-07,  50-278/98-07.)  The

NRC  “treated” this incident  as  a Non-Cited  Violation.

July  9-10,  1998 -  The  NRC  observed  “instrument  and  plant  control

personnel  failed  to  comply  with  the  technical  specification  action  time

requirements  fro  placing  ;  ‘A’  channel  of  the  main  control  room  emergency

ventilation  (MCREV)  system  in  trip  within  six  hours  of  making  the  channel

inoperable...This  non-reporting,  licensee  identified  and  corrected  violation  is

being treated  as  a Non-Cited  Violation...”  (IR  50-277/98-02,  50-278/98-02.)

- July  10-11,  1998 -  Power  was  reduced to  about  60%  at  Unit-2 for

condenser  waterbox  cleaning.

July  11,  1998 -  Unit  load  was  reduced to  74%  at  Unit-3 for main  steam

isolation  valve  testing.-  July  13,  1998  -  “A  reactor  level  water  excursion  on  July  13,  1998,

during  transfer  between  feedwater  control  system  computers  revealed  that

instrument  and  control  personnel  did  not  have  sufficiently  specific  written

guidance  or  criteria  on  computer  signal  differences  for  performing  the  computer

transfer.  Instrument  and  control  personnel  relied  on  inappropriate  assumptions

on  acceptable  computer  signal  differences.”  (IR  50-277/98-07,  50-278/98-07.)

(See  May  16  and  June  7,  1998,  for  related  incidents.)

- July  17,  1998 - AmerGen Energy announced that it  reached an

agreement with GPU to purchase TMI-1 for $100 million. The proposed

sale  includes  $23  million  for  the  reactor,  and  $77  million,  payable  over  five

years,  for  TMI-1’s  nuclear  fuel. (Background  information  can  be  found  on:

September  5  &  11  and  October  3,  1997,  and  May  5  &  27,  1998.)

July  17,  1998 -  “...the  2A  condensate  pump  had  to  be  shutdown  quickly

due  to  rapidly  climbing  temperatures  on  the  thrust  bearing.”  (IR  50-277/98-07,

5 0 - 2 7 8 / 9 8 - 0 7 . )

July  22,  1998  -  “...  hydrogen  water  chemistry  injection  into  the  unit  2

feedwater  system  unexpectedly  isolated  during  application  of  a  clearance  for  the

2A  reactor  feedwater  pump.”  (IR  50-277/98-07,  50-278/98-07.)

August  6-19,  1998  -  During  a  walkdown,  the  NRC  determined  “that  the

actual  wiring  did  not  match  the  schematic  drawings.  Although  the  schematics

showed that the  wiring for the MOVs [motor  operated  valves]  on  both  units  were

the  same, the  as-found  did  not match the  schematic  drawings for  3 CS  suction

MOVs.”   (IR  50-277/98-08,  50-278/98-08.)

“PECO  experienced  three  failures  of motor  operated  valves (MOVs)  during

2R12.  One  other MOV  was  in  a  significantly  degraded  condition  when  inspected.

All  of  these  MOVs  were  safety-related.”  (IR  50-277/98-10;  50-278/98-10;  NOV.)

(See  January  21,  1993,  for  a  related  incident.)

- August  10,  1998 -  During the  calibration  of the  ‘C’  detector, the

[chemistry]  technicians  inadvertently  removed  and  dropped  the  “D’  detector.

The technicians  performing this  work  did  not  stop  and  notify the  control  room

operations  personnel  or  Chemistry  Supervision  that  they  had  removed  the  “D”

detector  and  dropped  it...The  behavior  of the technicians to  not tell  details  about

the  event  for  several  days,  and  only  when  asked,  was  not  acceptable.  The

licensee  corrective  actions  were  narrowly  focused  on  the  chemistry  department

and  did  not  include  the  other  departments  at the  station.  Procedural  nonadherence  has  been  an  issue  at  the  station  for  the  past  year.” (IR  50-277/98-10,

5 0 - 2 7 8 / 9 8 - 1 0 . )

The NRC issued  a Violation.-  August  12,  19,  and  24,  1998 -  Access  and  alarm  failures  to  protected

areas  and  vital  door  areas  occurred  as  a  result  of  failures  with the  #1  security

multiplexer.  (IR  50-277/98-08,  50-278/98-08.)

August  14,  1998 - At  Unit-3,  a  loss  of  service  water to  a main  generator

hydrogen  cooler  resulted  in  a  reduction  of  unit  load to  84%.

August  19,  1998  -  at  Unit-3,  “Operators  entered  the  ‘B’  non-regenerative

heat  exchanger  room  and  found  the  heat  exchanger  vent  valves  partially  open,

instead  of  closed,  as  required.  Upon  further  investigation,  operations  personnel

identified that these  valves were  left  out  of  position  due to  poor  configuration

control  of  the  system  while  preparing  for  maintenance  activities.”  (IR  50-

277/98-08,   50-278/98-08. )

A Notice of Violation was issued.

August  20,  1998 -  The  Reactor Water  Cleanup (RWCU)  system  at  Unit-3

was  being  returned  to  service,  when  an  automatic  isolation  “occurred  due  to  a

high  flow  condition.”  (IR  50-277/98-08,  50-278/98-08.)

A Notice  of Violation was issued.

August 21,  1998 - Unit load was  reduced due to  a degraded  cooling of the

3C  main  transformer.  At  Unit  3,  “operators  commenced  a  down  power

maneuver  due  to  cooling  of  the  main  transformer.  The  reduced  load  prevented  a

loss  of  the  main  transformer  and  plant  transient  when  the  deluge  system

activated.”  (IR  50-277/98-08,  50-278/98-08.)

In  other words,  “The #6  oil pump had failed due to  a burnt wire  and when

then  operator,  following the  alarm  response  card,  switched the  local  control to

manual,  all  of the  cooling fans  and  oil  pumps tripped  off.”

August  22,  1998  -  An  operator  “inadvertently  shutdown  the  3C  drywell

chiller.  (IR  50-277/98-08,  50-278/98-08.)   The  NRC  concluded,  “An

engineering  evaluation  for  a  similar  event  that  occurred  on  March  25,  1997,

was  not  effective  to  preclude  the  August  22,  1998  event.”

August  23,  1998  -  “Weaknesses  in  maintenance  planning  and  work

practices  led to  a  significant  water  leak  on the  station  fire main  on August  23,

1998.  Water  from  the  leak  entered  the  safety  related  emergency  service

water/high  pressure  service  water  pump  house  via  underground  electrical

conduits  and  degraded  penetration  seals.”  (IR  50-277/98-08,  50-278/98-08.)

A Notice  of Violation  was  issued...-  August  23,  1998  -  “...  the  motor  driven  fire  pump  unexpectedly  started

during  the  post-maintenance  testing  of  the  H-1  fire  hydrant.  Neither  the  work

order  or  the  routine  test  procedure  contained  any  documentation  to  inform

operators  that  the  motor  driven  fire  pump  could  staff  during  the  hydrant  post

maintenance  testing  nor  did  these  documents  contain  instructions  to  fill  and

vent  the  fire  system  after  work  was  performed.”  (IR  50-277/98-08,  50-278/98-

0 8 . )

August  24,  1998 -  The  torus/drywell  vacuum  breaker  “lost  its  ‘seated  ‘

indication.”  Six  days  later,  although  required  by  technical  specifications,

“operations  personnel  determined  that  the  actions  to  verify  that  the  vacuum

breakers  were  closed  had  not  been  performed...”  (IR  50-277/98-08,  50-278/98-

08).

The NRC  “treated”   this problem  as  a Non-Cited  Violation.

September  3,  1998 - In the first  eight months  of  1998,  “PECO has  cut its

dividend  nearly  in  half,  announced  1,200  job  cuts,  and  written  off  $3.1  billion  in

assets.”  (Patriot  News, Bu s i n e s s, September 3,  1998. (See   June  13, 2001, for

more  job  reductions).

September  15,  1998  -  At  Unit-2,  the  reactor  water  cleanup  system

automatically  isolated.  PECO  found  that  this  incident  was  not   directly  related  to

an  event  that  occurred  on  December  1,  1998.  (IR  50-278/98-11,  50-278/98-11).

October  6,  1998 -  During  an  alternate  decay  heat  removal  test (ADHR),

“the  inspectors  observed  the  performance  of  an  abnormal  operating  procedure...”

(IR  50-277/98-10,  50-278/98-10; NOV.)

October  12-22,  1998  -  Three  fuel  movement  errors  occurred  during  this

period.  “These  errors  were  caused  by  a  failure  to  properly  verify  component

location  and  orientation  as  required  by  procedure.”  The  NRC  treated  this

incident  as  a  “no-cited  violation.”  (IR  50-277/98-10,  50-278/98-10; NOV.)  (See

October  22  and  24,  1998.)

October  14,  1998 - While  restoring the  2B  RHR [residual  heat  removal]

subsystem,  “operations  personnel  discovered  several  hundred  gallons  of  water  on

the  Unit-2  torus  room  floor.  After  further  investigation,  operators  discovered

that four  RHR  header  vent  valves  had  been  left  open  during the  performance  of  a

system  fill  and  vent  evolution...The  inspectors  determined  that  this  event  was

indicative  of  on-going  challenges  at the  station  in the  area  of  system  status  and

configuration  control.  Similar  issues  were  cited  in  Notices  of Violation  in  NRC

Inspection  Reported  50-277(278)/98-08  and  98-01.  The  inspector  concluded

that  PECO  did  not  not  have  sufficient  time  to  fully  implemented  corrective

actions for these  previous  issues. Therefore, this  event  was  not  subject to formal

enforcement  action.”  (IR  50-277/98-10,  50-278/98-10;  NOV.)

A Notice  of Violation  was  issued...-  October  16,  1998 -  “...during  a  routine  tour  of  the  reactor  building,  the

inspectors identified  a minor leak  on the 2  ’D’ RHR loop. (IR  50-277/98-10;  50-

278/98- 10;   NOV. )

October  22,  1998 -  “..the  refueling  floor  operators  removed  a  fuel  bundle

at  core  location  23-50  (southwest  orientation)  rather  than  the  the  specified  23-

52 (southeast  orientation.)  The  LSRO,  noting the  hole  left  by the  removed  fuel

bundle,  discovered  that  the  wrong  bundle  had  been  fully  removed  for  the  core.”

(IR  50-277/98-10;  50-278/98-10;  NOV.)   (See  October  12  and  October  24,

1998,  for  repetitive  incidents.)

October  24,  1998 -  “...core  alterations  were  suspended for  a third time

due to  a mis-oriented fuel  bundle in the  spent fuel  pool. (IR  50-277/98-10;  50-

278/98-10;  NOV.)  (See  October  12  and  22,  1998,  for  repetitive  incidents.)

October  25,  1998  -  At  unit-3,  the  “E33  bus  was  inadvertently  tripped

during  the  performance  of  a  surveillance  procedure  that  functionally  trip  tested

E32  and  E324  bus  over  current  relays.  This  resulted  in  an  ‘A’  channel  half

scram,  a full  reactor  water  clean  up  isolation,  loss  of the  ‘C’  standby  gas

treatment  fan,  an  inboard  primary  containment  isolation  system  group  3

isolation  and  subsequent  loss  of  reactor  building  ventilation,  and  a  half  primary

containment  isolation  system  group  1  isolation  that  did  not  cause  any  valve

motion.”

The  NRC  did  not  issue  any  violation.  “However,  inadequate  self-checking

and  peer  checking  by  the  instrument  and  control  technicians  performing  the

surveillance  procedure  were  determined to  be the  root  cause  of the  event.” (IR

50-277/98-10,  50-278/98-10;  NOV.)

October  28,  1998 -  The  NRC  identified  a  violation  which  “involved the

failure  of  the  radiation  protection  technicians  to  fully  comply  with  a  procedure

associated  with  source  checking  of  instruments  used  to  survey  incoming

shipments  of  radioactive  material.”

Additionally,  the  NRC  noted  that  there  56  “control  room  deficiencies”  and

“critical  control  room  deficiencies”  scheduled to  be  corrected  during the most

recent  refueling  outage.  (IR  50-277/98-08,  50-278/98-08.)

- October 28,  1998 - The use of  an improperly  sized jumper led to  an

unplanned  core  spray  loop  inoperability  and  “extended  the  inoperability  period

for  all  four  emergency  diesel  generators  (EDG).”  (IR  50-277/98-10,  50-278/98-

10;  NOV.)-  November  7,  1998  “...operations  personnel  in  the  Unit  2  control  room

observed  that  the  megawatt  electric  output  did  not  agree  with  the  reactor  core

thermal  power.”  (IR  50-277/98-11,  50-278/98-11.)The  NRC  “treated”  this

incident as a Non-Cited  Violation. (This was the fifth  Non-Cited  Violation

since  June  1998.  Please  refer  to  November  30,  1998,  and  July  27,  1999,  for

more data on  “Non-Cited  Violations” . )

November  17,  1998 -  “There  was  one  deficiency  identified  during  the

November  17,  1998,  plume  exposure  pathway  exercise  which  was  resolved  on

March  16,  1999,  during  a  remedial  [emergency  preparedness]  drill.  Also,  there

were  were  27  Areas  Requiring  Corrective  Action (ARCA)  identified...”   (FEMA

Final Exercise Report for the November 17, 1998, Peach Bottom Power Station Plume

Exposure Pathway Exercise.)

November  27,  1998 -  “...operators  shut  down  Unit  3 to  repair  a  nitrogen

leak  on  an  air  opened  valve  inside  the  drywell.” (See May  11,  2000,  for  a  related

incident).  (IR  50-277&278/98-11.)

- November  30,  1998  -  “...inadequacies  in  a  breaker  manipulation

procedure lead to an unexpected loss of one off-site power  source and  several

emergency  safety  feature  actuations.”  (IR  50-277/98-11,  50-278/98-11).  The

NRC  “treated” this  incident  as  a Non-Cited Violation. (This  was the sixth  NonCited  violation  since  June  1998).  (Please  refer  to  November  7,  1998,  and  April  6

&  July  27,  1999, for  data  on  “Non-Cited  Violations” . )

December  1,  1998 -  The  reactor  water  cleanup  system  “isolated  occurred

as  operators  were  opening  the  system  inboard  and  outboard  isolation  valves.”

According to  PECO,  his  event  was  not   directly  related to  an  incident that

occurred  at  the  RWCU  on  September  15,  1998.  (IR  50-277/98-11,  50-278/98-

1 1 ) .

December  6,  1998 - At Unit  3,  a  control  rod worth minimizer  rod  block

occurred  during  a  control  rod  drift  alarm  test.  (IR  50-277/98-11,  50-278/98-

1 1 ) .

- December  11,  1998 -  “A fire  watch  was found  asleep  in the  cable

spreading  room  by  inspectors.”  (IR  50-277/98-10;  50-278/98-10;  NOV.)  (See

December  18,  1993  and  August  4,  1994,  for  related  developments.)

December  11,  1998  -  “Contractor  personnel  performing  modification

work  on the  Unit-2  scram  air  header  exhibited  poor  foreign material  control

practices,  contrary  to  specific  work  order  instructions. Weaknesses  in  contractor

oversight  were  identified  by  these  poor  practices.  (IR  50-277/98-10,  50-278/98-

10;  NOV.)  (See  March  25  and  May  1,  1998,  for  related  incidents.)- December  19,  1998 - Unit load  at Unit 2  “was  reduced to 60% (See  also

January  2,  1999)  to  repair  a  leak  on  the  B3  feedwater  heater  extraction  steam

line.”  (IR  50-277/98-11,  50-278/98-11.)

December  27,  1998 - Both Units were  at  100% when  one (of two)

emergency  auxiliary  transformers  failed.  This  incident  precipitated  a  station

blackout  and  the  inoperability  of  an  off-site  power  source. (IR  50-277/98-11,  50-

278/98- 1 1 . )

December  30,  1998 - FEMA’s Final Exercise Report For The Spring  1998

identified  eight  Areas  Requiring  Corrective  Action  (ACRA).

December  31,  1998 -  PECO  reported  “a  charge  of  $125 million ($74

million  of  net  income  taxes)  for  its  Early  Retirement  and  Separation  program

relating  to  1,157  employees.”  (PECO  Energy  Company,  Form  10-K/A,  1999,  p.

7 7 ) .

January  2,  1999  -  Unit  load  was  reduced  again  (See  December  19,  1998)

to  65% to  allow  repairs to the main  steam turbine #3  control  valve. (IR  50-

279/98-11,  50-278/98-11.)  the  system  inoperable.”

January  19,  1999  -  “The  inspectors  reviewed  an  event  in  which  the  Unit

2 HPCI  system  gland  seal  condenser  lower  head  gasket  developed  a  significant

leak,  prompting  operators  to  declare  the  system  inoperable.”  (IR  50-277/99-01,

5 0 - 2 7 8 / 9 9 - 0 1 . )

January  21,  1999  -  “...the  station  made  a  four  hour  non-emergency  10

CFR  50.72  report to the NRC when  a damper in the flow path from the Unit 2

reactor  building  ventilation  to  the  standby  gas  treatment  system  (SGTS),  failed

to  open.”  (IR  50-277/99-01,  50-278/99--01.)

January  29,  1999 -  An  “outside  design  basis”  event (#  35335)  was

reported  for  Unit-2.  (See  August,  1999,  for  more  information.)

- February  1,  1999 -  The  NRC  issued  a Violation  and  stated their

“ c o n c e r n ” :

1) three  licensed  operators  failed  to  complete  your  facility  licensed

operator  requalification  program  for  the  period  April  1994  through

March  1996  and  the  training  was  not  made  up  until  April  1998,  in

some  cases;  2) the  failure  was  due  to  a  program  inadequacy

(systematic  cause)  and  the  inadequacy  apparently  caused  an

inaccurate  license  renewal  application  to  be  submitted  to  the  NRC

upon  which the  NRC  issued  a  renewed  operator  license.

(Curtis  J.  Cowgill,  NRC,  Chief,  Projects  Branch  4,  Division  of  Reactor  Projects.)-  February  1,  1999 - An  NRC  inspection team  found two  examples  in  which

RCIC [reactor  core  isolation  cooling]  system  design  basis  information  was  not

properly translated  into  procedures.”  A  Notice  of  Violation  was  issued. (50-

277/98-09,  50-278/98-09  &  NOV).

- February  8,  1999 -  During  Y2K testing  of the  Unit-2  rod  worth

minimizer  system,  a  “seven  hour  lockup  of  the  plant  monitoring  system (PMS)

computers  and  interruption  of  data to  PMS-supported  systems”   occurred.  The

problem  was  attributed  to  “an  information  systems  engineer [who]  did  not

adhere  to  station  policy  regarding  stopping  of  testing  when  unexpected

conditions  occur.”  (IR  50-27(278)/99-02.)

February  18,  1999  -  During  an  surveillance  test,  “the  3  B  core  spray

pump  breaker  malfunctioned  in  that  it  failed  to  close.”   (IR  50-277(278)/99-02.)

February  20,  1999 -  Unit-2,  “unit  load  was  reduced to  60% to  facilitate

control  rod  scram  time  testing,  reactor  feedwater  pump  turbine  testing,  a  main

steam  drain  tank  valve  repair,  and  a  control  rod  sequence  exchange.” (IR   50-

2 7 7 ( 2 7 8 ) / 9 9 - 0 2 . )

March  25,  1999 -  “NRC Inspection  Report  50-277 (278)/98-01  cited  a

violation  of the  Unit  3  operating  license for  exceeding the  licensed  power  level  by

as much  as 0.6% for  a period of  about  18 months. This  condition occurred  as  a

result  of  inaccurately  calibrated  feedwater  temperature  instruments.”   (IR  50-

277/99-01,  50-278/99-01.)  (See  related  developments  on  January  1  and  June

4,  1997,  and  May  1,  1998.)

March  27,  1999 -  Unit-2,  “unit  load  was  reduced to  62%  power to  allow

condenser  waterbox  cleaning  and  reactor  feedwater  pump  turbine  work.”  (50-

2 7 7 ( 2 7 8 ) / 9 9 - 0 2 . )

March 3,  1999 - The PUC voted  “to give PECO Energy Co. a  reproof for

running  misleading  advertisements  about  electric  competition  last  fall.”  (Patriot

N e w s,  March  5,  1999.)

- March 3-4,  1999 - Unit -3 was  reduced to 92% power for load drop

activities  and  “repair  a  minor  steam  leak  on  the  feedwater  level  switch  flange.”

( 5 0 - 2 7 7 / ( 2 7 8 ) / 9 9 - 0 2 . )

March  11,  1999 -  Documentation  of  two  Security  Level IV  violations  were

reported by the NRC:  1) Failure to Energize Trip  Relay for Main Control  Room

Emergency  Ventilation; and, 2) Failure  to  Properly  Maintain  Procedures  for

High  Pressure  Coolant Injection (HPCI)  System Manual  Operation.- March  12,  1999 - At unit-3,  “RCIC   [Reactor Core Isolation Cooling]

system  isolation  occurred  during  realignment  of  the  system  following  back

seating  of  an  inboard  steam  isolation  valve.”  (50-277(278)/99-02.)

March  18,  1999 - The potential for  a fire from flooding was identified  at

Units  2  &  3,  and  classified  as  an  “outside  design  basis”  event. (#35485.) (See

August,  1999,  for  more  information.)

In  addition,  “Between  March  and  October  1998,  PECO  engineering

identified  five  fire  areas,  containing  cables  for  safety-related  or  safe  shutdown

equipment  that  did  not  have  automatic  fire  detections  systems  as  required...” (IR

50-277  &  278/99-05.)

April  6,  1999 -  Security  staff  “detected  a  disabled  a  vital  door  area  door

alarm  in  Unit  3.  The  door  alarm  function  was  disabled  for  approximately  six

days...This  Security  Level  Violation IV  is  being  treated  as  a  Non-Cited  Violation,

consistent with Appendix C  of the NRC Enforcement Policy. (This was the  seventh

Non-Cited  Violation since  June  1998). (See  November  30,  1998,  for  related

events.)  (NCV-50-278/99-0401).”  (IR  50-277/99-04;  50-278/99-04).

- April  15,  1999  -  A  Fitness-for-Duty  incident  involving  controlled

substances  and three  used  syringes  was  reported to the  NRC. (See May  10,  1999,

for  results  of  laboratory  tests.)

April  17,  1999 -  “...Unit  3  load  was  reduced  to  approximately  83%  power

for  a  control  rod pattern  adjustment  and to  repair  an  air leak  on  a  control  rod

hydraulic  control  unit.”  (IR  50-277/99-04;  50-278/99-04).

April  25,  1999  -  “...a  high  temperature  alarm  (greater  than  500  degrees

F)  was  received  for the  Unit  3  control  rod  drive (CRD)  26-11.” (IR  50-277/9-04;

5 0 - 2 7 8 / 9 9 - 0 4 ) .

May  6,  1999 -  “During  the  inspection,  the  NRC  reviewed  a  violation  that

your  staff  identified  involving  the  Unit  2  rod  block  monitoring  system  being

inoperable  for  29  of the  185  control  rods.  Since this  finding  involved  a  Severity

Level III Violation of NRC  requirements, it  could be  considered for  escalated

enforcement  including  a  civil  penalty.”  (Exercise  of  Enforcement  Discretion

Related  to  IR  50-277;  278/99-02.)

“A  wiring  error dating  back to  original  construction was discovered

which  resulted  in  non-conservative  inputs to  channels  of the  Unit-2  rod  block

monitor for  29  of  185  control  rods.” (Bold  face  type  added.)  (50-277(278)/99-

0 2 . )- May 6,  1999 -  “PECO found a motor brake on the 2’C’ RHR [Residual heat

Removal]  pump  torus  suction  valve  that  should  have  been  removed  during  a

modification  in  1 9 8 8.  The  inspectors  were  concerned that  other  safety-related

MOVs included in the  1988 modification  could  have motor  brakes  installed.”

(Bold faced print added.)

Similar  time  delayed  problems  with  the  2’C’;  RHR  occurred  on  January  5

&  August  6-19,  1998.  Also,  see  January  21,  1993  for  root  cause  problems  with

the 2’C’ RHR.

- May  10,  1999 - PECO found traces of  a  controlled  substance  “in  a

bathroom  inside the  protected  area”  at  Peach  Bottom.  “The  results [from  a

laboratory]  indicated  the  presence  of  a  controlled  substance.”  (IR  50-277/99-04;

50-278/99-04).   (For  related  incidents  refer  to,  November,  1987;  January  8,

1988  &  February,  1988;  and,  November,  1989.)

May  15,  1999 -  “...Unit  2  load  was  reduced  to  approximately  71%  for

maintenance  on  an  outboard  main  steam  isolation  valve.”

“...Unit  3  load  was  reduced to  approximately  80%  power  of  a  control  rod

pattern  adjustment,  then  restored  to  100%  power”.   (IR  50-277/99-04;  50-

2 7 8 / 9 9 - 0 4 ) .

May  25,  1999 -  A  Unit-3  “reactor  operator  received  a  reactor  low  level

alarm  and  noted  that  the  level  was  trending  downward.  The  operator  took

prompt  actions  in  accordance  with  plant  procedures  to  reduce  reactor  power  and

to  manually  control  reactor  feed  pumps  until  level  had  stabilized.” (IR  50-277  &

2 7 8 / 9 9 - 0 5 . )

June  3,  1999 -  Plant  personnel  identified  “the  3B  core  spray  system flow

indicator  was  reading  zero  flow  with  the  pump  running.  I&C  [Instrumentation

and  Controls]  technicians  checked  the  valve  lineup  and  found  the  flow

transmitter  had  been  improperly  left  isolated  following  I&C  maintenance  the

previous  day.”   (IR  50-277  &  278/99-05.)

June 4,  1999 - Load  at Unit-2  “was  reduced to  about 65% power for main

condenser  waterbox  cleaning  and  various  maintenance  activities.”  Power  was

restored  to  100%  on  June  6,  1999.  (IR  50-277  &  278/99-05.)

June  10,  1999 -  Plant  “operators  experienced  a temporary  loss  of the  Unit

- 2  plant  monitoring  system  (PMS)  computer.  They  reduced  power  slightly  to

ensure  average  power  limits  were  not  exceeded,  since  the  average  power

monitoring function  of PMS  was  no  longer  available.” The  loss  of  safety

parameter  display  system,  was  reported  to  the  NRC  (IR  50-277  &  278/99-05.)-  June  11,  1999 - Load was  reduced  at Unit-3  “to  about 65% power for

scram  time  testing  and  other  maintenance  activities.”  Unit-3  achieved  full

power  two  days  later.  (IR  50-277  &  278/99-05.)

June  24,  1999 - Plant  personnel  “responded  effectively to  a Unit  3  RCIC

high  suction  pressure  alarm.  After  the  high  pressure  condition  was  corrected

through the  use  of the  alarm  response  card,  shift  personnel  continued to monitor

the  RCIC  system  for  abnormal  parameters.”  (IR  50-277  &  278/99-05.)

June 25,  1999 - Load was  reduced at Unit-3  “to about 85% power for a  rod

pattern  adjustment  and  was  returned  to  full  power  on  June  26.” (IR  50-277  &

2 7 8 / 9 9 - 0 5 . )

June  25,  1999 -  PECO’s  stock  price fell  $2.50  on  June  17  and  18,  1999

per  share  “after  management  warned  financial  analysts  second  quarter

earnings  were  trailing  expectations.

“During  a  conference  call  Thursday  discussing  AmerGen’s  agreement  to

purchase the Nine Mile Point  nuclear  power  plant  on Lake  Ontario  in New York

State  for  $163  million,  PECO  management  said  the  company  will  have  second

quarter  operator  earnings  of  about  31  cents  a  share...”  (Re u t e r s,  Jim  Brumm,

June  25,  1999.)  (See  September  11,  1997,  for  background  data  on  AmerGen,

and  refer  to May  12,  2000,  for  collapse  of  the  Agreement).

June  28,  1999   -  PECO  Nuclear  transferred  radioactive  waste  material  to

Chem  Nuclear’s  waste  disposal  facility  in  South  Carolina  “that  was  not  properly

characterized...The  issue...is  more  than  minor  in  that,  if  left  uncorrected,  it

could  become  a  more  significant  safety  concern  because  accurate  waste

characterization  is  necessary  to  ensure  proper  near-surface  disposal  of

radioactive  waste  materials.  The  issue  affected  the  Public  Radiation  Safety

cornerstone...this  is  considered  an  apparent  violation.”  (05000277  &

278/2000-002).  (See  April  25  &  August  3,  2000,  for  a  related  incident).

July to September,  1999 - Power was lost to the  351 line  on three

separate  occasions from  July to  September  1999  due to  storm  damage. The  loss  of

the 351 line  affects  a the  station blackout (SBO) line  and  results in  a loss of power

to the technical  support  center (TSC). The loss of power to the TSC  results in a loss

of  emergency  assessment  capability  and,  if  greater,  than  an  hour,  an  one  hour

non-emergency  report to the  NRC  if  required....In  response,  PECO  initiated  a

York  County  Reliability  Enhancement  Plan  to  address  immediate  reliability

issues for the  351  and  341 (a  backup  supply to the  351)  lines...” (IR

05000277/99008,   05000278/99008. )  -  July  7,  1999 -  “...operators  observed that the  ‘A’ ESW  pump flow  rate to

the  emergency  diesel  generators (EDGs)  was  in the In-Service  Test (IOST)  alert

range  specified  in  the  surveillance  procedure...Engineering  placed  the  ‘A’  ESW

pump  on  an  increased  testing  frequency  and  conducted  an  investigation  into

possible  causes  of the  degraded  flow.”   (IR  50-277/99-06;  50-278/99-06;  and,

7 2 - 1 0 2 7 / 9 9 - 0 6 ) .

July  10,  1999 -   “...Unit  3  load  was  reduced to  approximately  62%  for

main  condenser  tube  leak  repairs.”  (IR  50-277/99-06; 50-278/99-06; and,  72-

1 0 2 7 / 9 9 - 0 6 ) .

July  13,  1999 -  “...Unit  2  load  was  reduced  to  approximately  67%  power

as  a  result  of the trip  of   the  2B  reactor feed pump  and  subsequent  recirculation

system  runback.”   (IR  50-277/99-06;  50-278/99-06;  and,  72-1027/99-06).

July  15,  1999 -  At  Unit  3,  “operators  removed  the  fifth  stage  feedwater

heaters  from  service,  restoring  full  power  capability.”  (50-277/99-06;  50-

278/99-06; and  72- 1027/99-06) .

July  27,  1999 -  The  NRC  found  two  Severity  Level IV  violations  during

an inspection,  but  classified the infractions  as” (This was the eighth Non-Cited

V i o l a t i o n since  June  1998.  See  November  7  and  30,  1998  and  April  6,  1999,

for other  “Non-Cited  Violations.”).

“The  first  NCV  involved  the  inadvertent  loss  of  the  Unit  3  Auxiliary

Transformer  and  associated fast transfer  of four  4KV  emergency  busses  due to

inadequate  equipment  configuration  control  management  by  your  operating

staff  [May  21,  1999.]  The  second  NCV  involved  nonconformances  to  Peach

Bottom  Fire  Protection  Plan  which  were  self-identified  by  PECO  engineering

personnel  during  comprehensive  reviews  of  the  Fire  Protection  Plan.” (NRC,

Curtis  J.  Cowgill,  Chief,  Projects  Branch  4,  Division  of  Reactor  Projects.)

August,  1999 -  “If  a  utility  has  operated  a  reactor  outside  of the  safety

parameters  established  in  its  operating  license,  i.e.,  “outside  design  basis,”  it  is

required to  document  it  in  a  daily  event  report filed  with the  NRC.  The more

event  reports  filed  by  a  nuclear  eactor, the  less  certain that the  reactor  and  its

safety  systems  will  operate  as  designed.” (James  Riccio,  Public  Citizen, August,

1999, Executive  Summary.) (Refer to  October  20  1997  &  January  29  and March

18,  1999,  for  specific  “outside  design  basis”  events.)- August  4,  1999 -  The  NRC  reviewed  senior  reactor  operator  exams:

“A  performance  deficiency  was  identified  during  the  performance  of  a  JPM

applicant  when  an  applicant,  while  operating  the  refueling  bridge  under  the

direction  of  a fuel  handling  director (FHD),  allowed the mast to make  contact

with the  south  fuel  prep machine  handrail.  The mast  was  in the  normal  up

position  with  no  fuel  grappled.  Although the  contact  was minor  and  no  damage

resulted, the  event indicated  a  lack  of  oversight  on the  part  of the FHD  and

inattentiveness  on  the  part  of  the  applicant.”

“  An  exam  security  problem  was  identified  by  PECO  involving  exam

material  previously  copied  by  a  PECO  exam  team  member  and  later  discovered

in  the  same  copy  machine  by  another  PECO  exam  team  member.

“The  examiner  determined  based  on the time  line  developed  by  PECO,

through  interviews  with  those  involved,  and  reenactment  of  the  event,  that  the

event  was  minor  and  the  exam  was  not  compromised.”  (IR  50-277,278/99-301.)

September  1,  1999 -  “...while  installing  a  switch  for  a  Unit  3  refueling

outage  recirculation  pump  trip  modification,  a  contractor  technician

inadvertently  repositioned  the  3A  reactor  protection  system  (RPS)  alternate

power  supply  switch. This  resulted in  a temporary loss  of power to the 3As RPS,

causing  a  half  scram  and  ESF  actuation.”  (050277/99008,  05000278/99008.)

September  23,  1999 -  Unicom  and  PECO  announced  a  “merger  of  equals

with”  a  combined  value  of  $31.8  billion.  “The  new  holding  company  will  be  the

nation’s  largest  electric  utility  based  on  its  approximately  5  million  customers

and  it  will  have  total  revenues  of  $12.4  billion.” (PECO  Energy,  Press  release,

September  23,  1999.)  (See  (March  24  and  April  1,  2000,  for  related

de v e lopment s . )

September  20,  1999 -  “...while  increasing the  size  of  a  hole  in the  reactor

control  panel  to  support  a  Unit  3  refueling  outage  power  range  instrumentation

modification,  a  contractor  technician  drilled  into  a  wire  to  the  Unit  3B  reactor

manual  scram  circuit.  This  caused  a  blown  fuse,  a  half  scram,  and  the  resultant

ESF.”  (IR  050277/99008,  05000278/99008.)

September  30,  1999 - A turbine trip,  followed  by  a  scram,  occurred  at

Unit  2.  “Following  the  reactor  scram...a  heat  up  rate  of  170  degrees  in  45

minutes  occurred  in the  2A  recirculation  loop.  The  root  cause  of this  event,  as

presented  in the  licensee  event  report,  was  in  error  and  will  be  revised to  reflect

that  the  unreliable  bottom  head  drain  temperature  indication  prevented

starting  the  recirculation  pump.” Deemed  a  Severity  Level IV Violation, the  NRC  downgraded the  event to  a

Non-Cited  Violation. This was the ninth  Non-Cited  Violation since June

1998. ( IR  050277/99008,   05000278/99008. )

October  2,  1999 -   An unplanned isolation  of the  shutdown  cooling

occurred. (See (April,  200  and  September  24  &  October  2,  2000,  for  similar

incidents.)  (IR  05000277  &  278/2000-012.) -

October  6,  1999 -  leakage  of  reactor  coolant  system  water  into the  reactor

closed  cooling  water  system  was  caused  by  cracking  in  the  2”B’  recirculation

pump  seal  cooler. (See   March  15,  2000, for  problems  associated  with  increased

leakage).  (IR  05000277  &  278/2000-001).

October  12,  1999 -  PECO  “confirmed to the  NRC that the  corrective

actions  associated  with the  Thermo-Lag  fire  barriers  at  Peach  Bottom  had  been

completed.”  (PECO  Energy  Company,  Form  10-K/A,  1999,  p.  10.)(  See

September  24,  1994,  October  11,  1996,  May  19,  1998,  and  July  21,  2000,  for

related  material).

October  20,  1999 -  A  partially  open  main  steam  relief  valve  caused

reactor  cavity  water  to  leak  to  the  torus.  (IR  050277/99008,

0 5 0 0 0 2 7 8 / 9 9 0 0 8 . )

October  20,  1999 -  “An  engineering modification  error  caused the  flow

indication  for the  3A  recirculation  loop to  be  displayed  on the  wrong  indicator.”

( IR  050277/99008,   05000278/99008. )

October  21,  1999 -  Higher  than  expected  radiation  levels  were  monitored

in  the  reactor  cavity  after  drain-down.  The  source  was  the  placement  of  “newly

discharged fuel in  close proximity to the  spent fuel pool  gates.” (IR

0 5 0 0 0 2 7 7 / 1 9 9 9 0 0 9 ,   0 5 0 0 0 2 7 8 / 1 9 9 9 0 0 9   & 0 7 2 0 1 0 2 7 / 1 9 9 0 0 9 . )

November  2,  1999  -  “Although  PECO  engineering  was  aware  that  the

Unit-2  high-pressure  coolant  injection (HPCI)  steam  admission  valve  could  fail to

open  because  of  thermal  binding  when  the  system  was  isolated  for  maintenance,

engineering  personnel  failed  to  prevent  this  type  of  failure  during

maintenance...”  (IR  0500277/1999009,  05000278/1999009  &

0 7 2 0 1 0 2 7 / 1 9 9 0 0 9 . )-  November  8,  1999 -  during  an  NRC  inspection, two  violations  relating to

Engineering  Support  of  Facilities  and  Equipment  were  identified:

“The  failure  to  adhere  to  procedural  requirements  in  the  performance  of

ultrasonic  testing  of  safety-related  components  were  identified  by  the  inspectors

as  a  violation  of  NRC  requirements...The  failure  to  include  two  core  spray  system

welds  in the ISI  program  plan  was  an  violation...”

Both  violations  were  downgraded  an  rated  as Non-Cited  Violations.This

was  the tenth  Non-Cited  Violation since  June  1998.

- November  11,  1999 -A Non-Cited  Violation was  identified  when the

“2B  CS  pump  room  cooler  failed  to  start  during  a  routine  quarterly  surveillance

test.  Operations  personnel  determined that the  room  cooler fan  switch  was  not

fully  turned  to  the  ‘run’  position  which  prevented  the  fan  from  starting

automatically  when the  pump  was  started.”   PECO  also filed  a  LER.  This  was the

eleventh  Non-Cited  Violation since  June  1998.

( IR  05000277/ 1999009,   05000278/ 199009  &  07201027/ 199009. )

November  29,  1999 -  “...the  inspectors  discussed  with  plant  personnel

the  risk  significance  of  the   November  29,  1999,  Topaz  inverter  failure  that

caused  the  loss  of  the  alternate  shutdown  valve  control  function  at  the  alternate

shutdown  panel...Although  the  Unit  3  Core  Damage  Frequency  increased

slightly  due  to  this  failure,  the  Sentinel  on-line  risk  assessment  still  remained  in

the  ‘Green’  band.”  (IR  05000277/199009,  05000278/199009  &

0 7 2 0 1 0 2 7 / 1 9 9 0 0 9 . )

December  2,  1999 -   “...during  a  review  of  an  RHR  logic  system

functional test  procedure  prior to  a  planned test,  operations  personnel  discovered

that the test  procedure  simultaneously  caused  all  four  pumps to  be  incapable  of

starting  automatically  for  a  period  of  approximately  two  hours”  (IR

05000277/ 199009,   0500278/ 199009  &  0720/ 199009. )

The NRC issued a Non-Cited  Violation.This was the twelfth Non-Cited

Vi o l a t i o n since  June  1998.

December  19,  1999 -  PECO  Energy  filed  papers  before  the  Pennsylvania

PUC  to  acquire  Connectiv’s  (formerly  Delmarva  Power  &  Light  and  Atlantic  City

Electric)  share (15%)  of Peach Bottom  2 &  3. The  application was posted in the

Pennsylvania  Bulletin on  February  12,  2000. However,  “On  September  30,  1999,

the  Company  announced  it  has  reached  an  agreement  to  purchase  an  additional

7.51%  ownership  interest  in  Peach  Bottom  from  Atlantic  City  Electric  Company

and  Delmarva  bringing  the  Company’s  ownership  to  50%.”  (PECO  Energy

Company,  Form  10-K/A,  1999,  p.  11).

(See  October  19,  2001,  for  a  related  acquisition  by  PSE&G).- December  27,  1999 - The NRC  acceded to industry  pressure to  keep

information  about  nuclear  plant  shutdowns  and  restarts  “confidential”  unless

the  licensee  “waives  the  right.”   “In  the  past,  the  NRC  would  supply  information

about most  aspects  of  nuclear  licensees’  affairs,  but  with the move toward

market  competition,  it  became  evident  that  the  policy  was  having  an  effect  on

wholesale  prices...The  NRC’s Mindy  Landau  said,  ‘We  have  seen  shutdown

information  directly  affect  the  prices  on the  spot market  for  electricity.  ‘  “ (The

Energy  Report,  December  27,  1999.)

December  29,  1999 -  “...Unit  2  load  was  reduced  to  approximately  70%

power to  support  grid  conditions for the millennium  roll  over.” (IR

0 5 0 0 0 2 7 7 / 1 9 9 9 0 1 0 ,   0 5 0 0 0 2 7 8 / 1 9 9 9 0 1 0   &  0 7 2 0 1 0 2 7 / 1 9 9 9 0 1 0 . )

January  2000  -  “...an Instrument  and  Controls  (I&C)  technician  found

that  the  existing  4KV  emergency  bus  degraded  grid  relays  could  not  be

calibrated  to  a  new,  higher  voltage  setpoint  in  a  revision  to  technical

specifications...Engineering  personnel  determined  that  the  causes  were

deficiencies  in  procedure  adherence,  attention  to  detail,  and  design  review

during  the  modification  process  and  they  initiated  appropriate  corrective

ac t ions . ”   ( IR  0500277/ 199910,   05000278/ 1999010  &07201027/ 1999010. )

January  12,  2000  -   “A  contract  painter  inadvertently  bumped  an  E4

emergency  diesel  generator  coolant  expansion  tank  drain  valve,  resulting  in  a

partial  drain  down  of  the  coolant  expansion  tank.  The  emergency  diesel

generator  remained  operable.  The  problem  was  similar  to  a  recent  previous

event.”

The  NRC  “determined”  this  incident  was  a  “minor  violation.” (IR

0 5 0 0 0 2 7 7 / 1 9 9 9 0 1 0 ,   0 5 0 0 0 2 7 8 / 1 9 9 9 0   &  0 7 2 0 1 0 2 7 / 1 9 9 0 1 0 . )

January  19,  2000 -  “Procedure  errors  with  a  Unit  2  high  pressure

coolant injection (HPCI)  system tests led to  a longer-than-planned period  of

unavailability  for  the  HPCI  system.  The  system  manger  conducted  a  thorough

investigation  of  the  problem  and  concluded  that  incomplete  reviews  during  the

revision  process  failed  to  identify  the  procedure  errors.”  (IR  05000277/199010,

05000278/ 19990  &  07201027/ 199010. )

January  21,  2000 -  “...Unit  2  load  was  reduced  to  approximately  65%  for

condenser  water  box  cleaning  and  a  control  rod  pattern  adjustment.” (IR

0 5 0 0 0 2 7 7 / 1 9 9 9 0 1 0 ,   0 5 0 0 0 2 7 8 / 1 9 9 9 0 1 0   &  0 7 2 0 1 0 2 7 / 1 9 9 0 1 0 . )

January  26,  2000  -  “...a  Unit  3  turbine  building  equipment  operator

identified  a degrading  condition  on the  3’B’ RPS flexible  coupling.” (IR

0 5 0 0 0 2 7 7 / 1 9 9 0 1 0 ,   0 5 0 0 0 2 7 8 / 1 9 9 9 0 1 0   &  0 7 2 0 1 0 2 7 / 1 9 9 0 1 0 . )-  February  6,  2000 -  “...during  the  transfer  of  a  non-safety  4KV  circuit

breaker  on the 2”b”  control  rod drive (CRD) pump, the breaker did not  close  as

expected  due  to  a  mechanical  failure  of  the  anti-pumping  relay.”   (IR  05000277

&  278/2000-001 ) .

February  25,  2000 -  “...Unit  3  load  was  reduced  to  approximately  63%

power  to  perform  a  control  rod  pattern  adjustment,  scram  time  and  primary

containment  isolation  system  testing  and  replacement  of  the  outboard  main

stream  isolation  valve  DC  solenoid  valves”.   (See May  11,  2000,  for  a  similar

challenge).  (IR  05000/277  &  278/2000-001).

March  4,  2000 -  “...Unit  2  load  was  rescued to  approximately  65%power

for  condenser  water  box  cleaning.”  (IR  05000277  &  278/2000-001).

March  15,  2000 -  “...the  Unit  2 HPCI  steam  admission  valve (MO-2-23--

014) failed to  open when  operations  personnel  attempted to  align the HPCI

system  for  post-maintenance  testing.  PECO  determined  that  this  event  was

caused  by  thermal  binding  of  the  valve  disk  in  its  seat.  A  similar  event  had

occurred  in  November  1999  and  was  documented  in the  NRC Inspection  Report

50-277(278)/9908.  Several  corrective  actions  were  initiated  for  the  November

event,  included  plans  to  upgrade  the  valve  motor  and  placing  the  valve  in  a

Maintenance  Rule  (a)(1)  status  in  February  2000.  (IR  05000277  &  278/2000-

0 0 1 ) .

March  15,  2000 -  “Leakage  from the  reactor  coolant  system  water  into

the  reactor  building  closed  cooling  water  system (RBCCW)  increased to

“approximately  4.125  gallons  per  hour”.  (See  October  6,  1999,  for  background

information).  (IR  05000277  &  278/2000-001).

March 22, 2000 -  “...Unit 2 load was  reduced to less than 20% power to

allow  personnel  to  enter  the  drywell  and  repair  an  instrument  nitrogen  leak.  All

Unit  2  inboard main  steam  isolation  valves  DC  solenoids  were  replaced  during

this  load  drop.” (See May  11,  2000, for  a  similar  challenge  at  Unit  3). (IR

05000277  &  278/2000-001).

- March  23,  2000 -  “...while the HPCI  system  was  inoperable for

surveillance testing, the  Unit HPCI MO-16  would  not  re-open  after  being taken to

the  shut  position.  Troubleshooting  revealed  that  this  failure  was  caused  by  high

resistance  associated  with  a  contact  in  the  open  logic  circuit. Maintenance

personnel  cleaned the  contact  and  initiated  actions to  replace  it.

“A  similar  event  occurred  in  November  1998,  when  the  same  valve  (MO-

16)  on Unit  2 failed to  close  due to  an  auxiliary  contact  problem. The  contacts for

this  valve  were  recently  removed  for  analysis  during  a  scheduled  maintenance

activity  on  March  15,  2000.   The  cause  of  this  failure  was  under  investigation

(PEP  10009425)  at  the  time  of  the  Unit  3  failure...“...Engineers  appropriately  recognized  the  possible  recurring  nature  of

this  issue  and the  potential  impact  on  system  operability  for  similar  failures  on

other DC motor-operated  valves in the HPCI  and  reactor  core isolation  cooling

systems.  The  inspectors  noted  that  auxiliary  contact  failures  have  occurred  in

several  safety  and  non-safety  related  valve  breakers  over  the  past  few  years.

These failure  have  been  documented  in NRC Inspection  Reports  50-

277(278)99006,  98001  and  97005.  (IR  05000277  &  278/2000-001).

March  24,  2000 -  PECO  Energy  reached  a  comprehensive  settlement

with  parties  intervening  in  the  proposed  Unicom  merger.  “The  Company

reached  agreement  with  advocates  for  residential,  small  businesses  and  large

industrial  customers,  and  representatives  of  marketers,  environmentalists,

municipalities  and  elected  officials.” (PECO  Energy,  Press  Release, March  24,

2000.)  (See  September  23,  1999  and  April  1,  2000,  for  related  developments.)

March  25,  2000  “...Unit  2  load  was  reduced  to  approximately  66%  power

due  to  problems  with  the  4’C’  feedwater  heater  lever  control. (IR  05000277  &

2 7 8 / 2 0 0 0 - 0 0 1 ) .

April, 2000 -    An unplanned isolation  of the  shutdown  cooling  occurred.

(See  September  24  &  October  2,  2000,  for  similar  incidents.) (IR  05000277  &

2 7 8 / 2 0 0 0 - 0 1 2 . )

April  1,  2000 -  “Following the merger  announcement, the  shares  of  both

firms  dropped,  indicating  the market’s  clear  disapproval  of  the merger.  PECO  fell

4.4  percent  and  Unicom  fell  2.2  percent  on  the  day  of  the  announcement...After

60 days, the  shares of both firms were  still below the pre-deal prices. PECO has

lost  over  $1  billion  in  market  capitalization.  Unicom  lost  nearly  $600  million.

PECO  shareholders  lost  more  than  Unicom,  reflecting  the  market’s more  positive

initial  view  of  of  PECO. The market  seems to think that the  association  with

Unicom  may  decrease  PECO’s  performance.”  (Public  Utilities  Fortnightly,  April

1,  2000.)  (See  September  23,  1999  &  March  24,  2000,  for  related  incidents.)

April 25, 2000 -   The NRC  “determined that PECO Nuclear did not

confirm  or  verify that the  leak testing  gauges  used for  preparation  of  a  Type B

shipping  cask...conformed  to  accuracy  requirements...The  issue  of  PECO

Nuclear’s  ability to  assure  proper  closure  and  leak testing  of  shipping  casks  is

more than  a minor issue  since  such inabilities  could  be  a  precursor to more

significant  events.”

The NRC deemed this infraction a Non-Cited  Violation. This was the

thirteenth  Non-Cited  Violation since  June  1998.(IR  05000277  &  278/2000-

002).  (See  June  28,  1999  &  August  3,  2000,  for  related  incidents.)   May  2,  2000  -  “...a  supervisor  at  the  York  County  ‘911’  center

inadvertently  activated  the  York  County  portion  of  the  alert  and  notification

sirens”.  (IR  05000277  &  278/2000-002).

May  7,  2000 -  “Unit  2  load  was  reduced to  approximately  90%  power

after  the  2  ‘A’  circulating  pump  was  removed  from  service  due  to  high  motor

upper  guide  temperatures.”  (IR  05000277  &  278/2000-002).

May  10,  2000 -   “Unit  3  load  was  reduced to  approximately  35%  power

after the  3  ‘B’  recirculation  pump  was  removed from  service  due to  low motor  oil

level”.  (IR  05000277  &  278/2000-02).  (See  May  11,  2000,  for  related

inc ident s ) .

May  11,  2000 -  “Unit  2  load  was  reduced to  approximately  98%  due to

unexpected  speed  changes  on the  2  ‘B’  recirculation  pump  while  raising  or

lowering  pump  speed.”  (IR  05000277  &  278/2000-002).  (See  May  15  and  19,

2000,  for  related  incidents.)

May  11,  2000 -  “Unit  3  power  was  further  reduced  to  approximately  19%

on to  allow  entry  into the  drywell to  support  adding  oil to the  3’B’  recirculation

pump  motor,  repair  of  an  instrument  nitrogen  leak,  and  replacement  of  all

inboard  main  steam  isolation  valves  DC  solenoids”.  (IR  05000277  &  278/2000-

002).  (See  November  27,  1998,  February  25  and  May  11,  200,  for  related

problems.  Also,  refer  to  June  1,  1998  and March  22,  2000,  for  similar

challenges  at  Unit  2).

May  12,  2000 -  “Niagara Mohawk  Power  Corp.  said  on  Friday that

agreements  to  sell  its  nuclear  assets  to  AmerGen  Energy  Co.  have  been  mutually

ended  by  the  two  companies.”  (See  June  25,  1999,   for  background  information.)

May  13,  2000 -  The  National Weather  Service  reported  that  a  tornado

touched  down  in  the  Peach  Bottom-area.

May  15,  2000 -  “Unit  2  load  was  reduced to  approximately 86% to  isolate

the  ‘B’ feedwater  heater  string  due to  a  leak  in the  ‘B2’ feedwater  heater.” (IR

05000277  &  278/2000-002).  (See  May  11  and  19,  2000,  for  related  incidents).

May  19, 2000 -  “Unit 2 was placed in  cold  shutdown (Mode 4) to facilitate

repairs  of  the  ‘B2’  feedwater  heater  tube  leaks.”  (IR  05000277  &  278/2000-

002).   (See  May  11  and  15,  2000,  for  related  incidents).

May  22,  2000 - At Unit  2,  “a  steam  leak was  discovered in the  piping

from the  ‘F’ moisture  separator to the  ‘B’  low  pressure turbine.  The turbine  was

removed  from  service  on May  22  and the  leak  was  repaired.  Unit  2  returned to

100%  power  on  May  23.”  (IR  05000277  &  278/2000-006  &  07201027/2000-006).

May  27,  2000 -  The  United  States  Department  of  Justice,  “filed  an  action

claiming  breach  of  contract  against  the  Company  in  the  United  States Middle

District  of  Louisiana  arising  out  of the  Company’s termination  of the  contract to

purchase  Cajun’s  30%  interest  in  the  River  Bend  nuclear  power  plant.  The  action

seeks the full  purchase  price  of the  30%  interest  in the  River Bend  nuclear  power

plant,  $50  million,  plus  interest  and  consequential  damages.  While  the  Company

cannot  predict  the  outcome  of  this  matter,  the  Company  believes  that  it  validly

exercised  its  right  of termination  and  did  not  breach the  contract.”   (PECO

Energy  Company  1999  Annual  Report,  p.  46).  (See  June  5,  1997  and  May  27,

1998,  for  background  information).

May  28,  2000 -  “The  most  recent  packing  gland  follower  cracking  event

occurred  on  a  similar  Unit  3  root  isolation  valve  on May  28  ,2000  and  resulted

in the  leakage  of  contaminated  reactor  coolant  system  water  outside  of the

primary  coolant.  Leakage  of  contaminated  reactor  coolant  system  water  outside

of  the  primary  containment  is  a  significant  condition  adverse  to  quality.”  (See

August  7,  2000,  for  more  problems  with  packing  gland  follower  cracking.”   (IR

05000277  &  278/2000-008)

- BLACKOUTS & HIGH PRICES: SUMMER 2000

-  April  11,  2000 -  The  North  American  Reliability’s  Council’s (NERC)

General  Counsel,  David  Cook, testified  before  a  Senate  Committee,  and  “repeated

findings  of  a  recent  NERC  survey that  several  control  area  operators  in the

Eastern  Interconnection  were  ‘leaning’  on  the  interconnection  during  nine  peak

hours (i.e.,  selling  energy that they didn’t have). (Public  Utilities  Fortnightly, May

15,  2000,  p.  16)

-  May  9,  2000  -  “The  Pennsylvania-New  Jersey-Maryland  (PJM)  power

pool  implemented  a five  percent  voltage  reduction  on May  9 to  ease  pressure  on

the  distribution  system.

“The  action  was  taken  to  avoid  emergency  rolling  blackouts  where  power

is  interrupted  for  short  durations - typically  20 to  30 minutes.” (Up d a t e, The

Department  of  Environmental  Protection,  May  12,  2000,  p.  2).

-  May  16,  2000  -  The  electric  utility  industry  predicted  a  17%  difference

between  supply  and  demand  in  a  service  area  stretching  from  Virginia  Beach  to

De t roi t .

“The  all  time  maximum  PJM  demand  of  51,700 MWQ  occurred  on  July  6,

1999.”  (PECO  Energy  Company,  Form  10  K/A,  p.7).

June  28,  2000  -  “This  summer,  (residential  customers)  probably  have

fewer  choices than they  did  a few months  ago,  and the  choices they  do  have  are

more  expensive  than  they  were...Combine  strong  economic  growth  with  hot

weather  and the  bad  luck  of  having things  like  a  number  of  power  plants  being

shut  down  at  the  same  time  because  of  outages,  and  you  certainly  have problems.” (Sony  Popowsky,  Consumer  Advocate, Investor’s  Business  Daily) .

In  June,  San  Francisco  suffered  a  blackout,  and  California  has mandated

usage  restrictions  for  commercial,  industrial,  and  residential  customers.

-----

June  9,  2000 -  The  NRC  “approved transferring the  operating  license for

the  Oyster  Creek  nuclear  station  in  New  Jersey  to  AmerGen  Energy  Co.”  The

New  Jersey  utilities  board,  which   will meet  on  June  22,  still  needs to  approve

the  transfer.  (“Reuters”,  June  9,  2000,  3:12  pm.)  (See  September  11,  1997,  for

background  information.  Refer  to  August  16,  2000,  for  follow-up  problems).

July  20,  2000 -  “U.S.  Energy  Secretary  Bill  Richardson  on  Thursday  said

the  government has  agreed to  allow PECO Energy Co. to defer up to $80 million

in  nuclear  waste  fee  payments  for  its  Peach  Bottom  plant  in  Pennsylvania,  to

compensate  for  the  Energy  Department’s  failure  to  store  its  waste...The  deal

allows PECO to  reduce the projected  charges passed into the Nuclear Waste Fund

to  reflect  costs  reasonably  incurred  by  the  company  due  to  the  department’s

delay.”  Press  Release,  U.S.  Department  of  Energy.  July  20,  2000.)

July  21,  2000 -  “During  the  inspection, [April  14-18,  2000]  the  NRC

identified two findings  associated  with the  adequacy  of  post-fire  safe  shut  down

equipment  circuit  analyses  at  the  station.  Both  of  these  issues  were  determined

to  be  apparent  violations...It  is  our  understanding that  you  do  not  consider  either

of these two issues to be violations of  10 CFR 50 or your operating license.

Additionally,  we  recognize  that  other  commercial  nuclear  power  plant  operators,

represented  by  the  Nuclear  Energy  Institute  (NEI),  have  adopted  a  similar

position  regarding  these  issues.  As  such,  in  accordance  with  our  current

enforcement   policy...the  NRC  will defer  any further  enforcement  action

relative to these  issues  until the  staff  evaluates NEI’s  proposed  resolution

methodology.”  Wayne  D.  Lanning,  NRC,  Director,  Division  of  Reactor  Safety.

(See  May  19,  1998  and  October  12,  1999,  for  related  events.)

August 3, 2000 - PECO was  assessed  a  “White” level Violation for its

“failure  to  properly  classify  radioactive  waste  for  shallow  land

burial...Specifically,  the  shipment  was  identified  as  Class  A  waste  containing  99

curies  when  it  should  have  been  classified  as  Class B  waste  containing  407

curies.” (NRC,  Hubert  J. Miller,  Regional  Administrator).   (Refer  to  June  28,

1999,  for  background  information.  See  April  25,  2000,  for  a  related  incident.)

August  7,  2000  -  Unit  3  “automatically  shutdown  from  100%  power

when  a  one  inch  instrumentation  rack  root  valve  packing  gland  follower  failed

and  caused  a false  reactor  low  level  input  into the  RPS [reactor  protection

system].  The  failure  occurred  when  the  packing  gland  follower  broke  into  two

pieces  allowing  package  leakage  of  contaminated  reactor  coolant  system  water

from  the  instrumentation  piping.  The  leak  was  immediately  isolated  by

actuation  of  the  excess  flow  check  valve  in  the  instrumentation  piping  line.  Unit

- 3  also  experienced  Groups II  and III  primary  containment  isolation  valve  closures due to the false  reactor  low  level  signal.”

The NRC issued a Non-Cited  Violation.This was the fourteenth NonCited  Violation since  June  1998.

The  NRC  also  criticized  PECO’s  corrective  action  program: “Two  previous

packing  gland  follower  cracking  incidents  had  occurred  on  similar  valves  at  the

facility  during  the  past  eighteen  months.  The  most  recent  packing  gland  follower

cracking  event  occurred  on  a  similar  Unit  3  root  isolation  valve  on May  28,

2000  and  resulted  in  the  leakage  of  contaminated  reactor  coolant  system  water

outside  of  the  primary  coolant.  Leakage  of  contaminated  reactor  coolant  system

water  outside  of  the  primary  containment  is  a  significant  condition  adverse  to

quality.The  identification  of  this  significant  condition  adverse  to  quality  was  not

adequately  documented  in  PECO’s  corrective  action  system,  and  as  a  result,  the

cause  of the  condition  was  not  determined,  corrective  actuation  was  not taken to

prevent  repetition,  and  generic  concerns  with  potential  packing  gland  follower

cracking  on  other  valves  were  not  addressed.”  (IR  05000277  &  278/2000-008)

- The NRC issued a Severity  Level  IV  violation “related to the

identification  and  resolution  of  problems  on  leakage  of  contaminated  reactor

coolant  system  water  caused  by  cracking  of  instrument  root  valve  packing  gland

followers.”

August  14,  2000  -  AmerGen   reported  a  valve  failure  [reactor  building

isolation  valves]  at  Oyster  Creek  that  forced  the  plant  to  shutdown  at  82%

power.  “It’s too  premature to  guess  at  a  date the  unit may  return. We’re  still

evaluating  the  problem  and  will  likely  replace  the  valves  that  failed,  “  AmerGen

Spokeswoman,  Debra  Piana.  (“Reuters”,  August  16,  2000.)  (Please  refer  to

September  11,  1997  and  June  9,  2000  for  additional  information.)

- August 22, 2000 - The NRC issued a Non-Cited  violation  related to

“inservice  tests  for  the  standby  liquid  control  pumps.  A  two-minute  wait  was  not

mandated,  as  required  in the  applicable  Code,  by the test  procedure  before  pump

flow  and  pressure  measurements  were  recorded.  Because  of  the  very  low  safety

significance, the  violation  was  non-cited.”  This  was the fifteenth  Non-Cited

Violat ion since  June  1998. (NRC, Wayne  D.  Lanning,  Director,  Division  of

Reactor  Safety,  IR  05000277  &  278/-005.)

August 23, 2000 -    “Operators   reduced power [at Unit 2] to

approximately  68%  to  remove  the  ‘B’  feedwater  heater  string  from  service  due  to

suspected  leaks  and  on August  24  returned the  unit to  83%  power.”   (See

September  7  &  13,  2000,  for  related  incidents.)  (IR  05000277  &  278/2000-

0 1 0 . )- September 7, 2000 -    “Operators   reduced power [at Unit 2] to

approximately  16%  in  response   to  pressure  perturbations  in  the  ‘B’  feedwater

heater  string  and  on   September 8   returned the  unit to  75%  power.”   (See

August  23  &  September  13,  2000,  for  related  incidents.)  (IR  05000277  &

2 7 8 / 2 0 0 0 - 0 1 0 . )

September  13,  2000 -    Operators   reduced  power to  approximately  16%

at [Unit  2]   in  response to  pressure  perturbations  in the  ‘B’ feedwater  heater

string  and  on  September  8  returned the  unit to  75%  power.” (See August  23  &

September  7,  2000,  for  related  incidents).  (IR  05000277  &  278/2000-010.)

September  15,  2000 -  “...with  Unit-2   at  approximately  16%  power  and

24%  flow,  operators  performed  a manual  scram  to  prevent  operation  in  the

restricted  zone  of the  power flow map  after  an unplanned trip  of the  2B  reactor

recirculation  pump.“  (IR   05000277  &  278/2000-012.)

September  16, 2000 -    Three workers failed to follow  oral  and written

instructions,  and  “either  worked  in  proximity  of  ,  passed  through,  or  transported

radiation  shielding  materials  through  elevated  radiation  fields  (up  to  13.9  R/hr)

in the  drywell. As   a  result,  one  of the workers  did not  contact  radiation

protection  personnel  upon  alarm  of the  dosimeter,  also  as  specified  in  written  and

oral  radiation  protection  instructions.

“This issue was  considered to  be  of  very low   safety  significance...a N o n -

cited  violation “ was issued. This was the sixteenth  Non-Cited  Violation since

June  1998.  (IR  05000277  &  278/2000-010.)

August  31,  2000 - Exelon  issued  an  LER  after  determining that three  of

four  EDGs  “were  inoperable  during  the  summer  of  1999,  based  on  their  inability

to mitigate  a postulated loss-of-coolant-accident plus loss-of-off-site-power design

basis  accident  for  a  maximum  of  approximately  25  hours.  The  licensee

attributed the  cause  of the  event to  be  an  original  design  deficiency  on the EDGs,

which  allowed  cross-flows  between  the  jacket  water  coolers  and the  intake-air

coolers.”   (IR  50-277/01-06,  50-278/01-06.).

September  24,  2000 -  During  the  2R13  refueling  outage,  a  “spurious”

unplanned  isolation  of the  shutdown  cooling  occurred. (See  October  2,  2000, for

similar  incidents.)   (IR  05000277  &  278/2000-012.)

September  28,  2000 -   “...operations  personnel  determined,  during  inservice  testing,  that  ESW  [Emergency  service  water]  check  valve  2-33-514

failed [sic]  open. The  check  valve  is  designed to  prevent  reverse flow from the

safety-related  ESW  into  the  Unit  2  non-safety  related  water  service  system.

Operators declared both ESW  systems inoperable, because ESW flow to the EDGs

and  emergency  core  cooling  system  room  coolers  and motor oil  coolers  could be

i n a d e q u a t e . . . ”“The  inspectors  and  operations  personnel  noted that,  during two  periods  in

which the ESW  system  was  declared  inoperable,  operators  did  not  address the

operability  status  of the  EDGs  or  associated  Technical  Specifications  action

statements  and/or  applicable  limiting  conditions  for  operation  of  Unit  2  which

was  in Mode  5 (refueling)  at  the  time...”

”The  inspectors  determined  that  this  event  required  further  evaluation  in

the  significance  determination  process.”  (See  October  1  through  November  18,

2000,  for  an  identical  problem).   (IR  05000277  &  278/2000-010.)

September  30,  2000 -  Operators   reduced  power to  approximately  18%  in

response to  a low  oil level in the  3B  recirculation pump motor. Unit  3 was  at

approximately  35%  power.”  (IR  05000277  &  278/2000-010.)

October  1  through  November  18,  2000  -   “Emergency  service  water

(ESW)  system  check  valve  2-33-514  failed  [sic]  open,  allowing  safety-related

ESW  flow  to  be  partially  diverted  from  emergency  diesel  generators(EDGs)  and

emergency  core  cooling  system  room  coolers.  The  inspectors  and the  licensee

identified that this  risk  important  component  had  not  been  included  in  a

preventive  maintenance  program.

“This issue  caused the ESW  system and the EDGs to be degraded for a

period  of  up two  years.  This finding  was  of  very  low  safety  significance  because,

although the ESW flow  rate to the EDGs  was  below the  design  basis minimum

value  engineering  personnel  determined  that  the  EDGs  would  have  remained

available  during  accident  conditions.”  A  Non-Cited  Violation  was  issued.”

- This was the seventeenth  Non-Cited  Violation since June  1998. (See

September  28,  2000,  for  a  related  incident.)  (IR  05000277  &  278/2000-012.)

October 2, 2000 -   Three unplanned isolations of the  shutdown  cooling

(SDC)  occurred.  “Engineering  personnel  stated  that  these  events  were  caused,  in

part,  by  an ILRT (Integrated  Leak  Rate  Test)  procedure that  did  not fully  account

for  the  reduced  operating  margin  to  the  high  pressure  isolation  setpoint...”

“At the time  of the isolations during the ILRT, SDC was the  only  operable

decay  heat  removal  system...”

Continued on the following page...   “The  inspectors  identified that there  were  previous  occurrences  of  SDC

isolations  on  Unit  2 that  were  not  fully  investigated.  For  example,  on  October  2,

1999,  a  similar  SDC  isolations  occurred,  but  no  cause  was  identified.  The

pressure  switches  were found to  be  in  calibration. No  PEP  corrective  action  plan

document  was  initiated.  Further,  in  April  2000,   engineering  personnel  initiated

an  action item to troubleshoot isolations,  but no  action had  been taken prior to

the  outage.  The  inspectors  brought this  issue to the  attention  of  engineering

management.  Engineers  also  noted  that  there  were  two  other  not-fullyunderstood  SDC  isolations  on  Unit  2  since  1994. The  inspectors  concluded that

engineering  personnel  had  missed  opportunities  to  investigate  previous  SDC

isolations  and  this  constituted  a  corrective  action  performance  issue.”

The inspectors did not identify  a  violation of NRC  requirements.

(See  September  24,  2000,  for  related  incident.)   (IR  05000277  &  278/2000-

0 1 2 . )

- October  4,  2000 -  Unit-2  was taken  critical.

October  4,  2000 -  Unit-2  “operators  halted the  reactor  startup following

the  discovery  of  a missed  post-maintenance test  on  a  control  rod.” (IR  05000277

&  278/2000-012. )

October  17,  2000 -  Unit-2  “operators  reduced  power to  approximately

65% to  repair  a  condenser tube leak. The unit was  restored to  100%  on October

18.”  (IR  05000277  &  278/2000-012.)

October  22,  2000 -  “...the  failure  of  the  Unit-2  ‘H’  torus/drywell  vacuum

breaker  to  fully  close  during  surveillance  testing  rendered  primary  containment

inoperable...Unit  load  was  reduced  to  16%  due  to  an  inoperable  torus/drywell

vacuum  breaker...Because  of  the  very  low  safety  significance  of  this  item  and

because the  licensee  has  included  it  in their  corrective  action  program (PEP

- I0011883), this  procedure  violation  is  being treated  as  a  Non-Cited

Violation.” This was the eighteenth Non-Cited  Violation since June 1998 (IR

05000277  &  278/2000-012. )

October  23,  2000 -  Unit-2  was  shut  down to  repair the torus/drywell

vacuum  breaker.  The  reactor  was  taken  critical  on  October  24  and  unit  load  was

100%  on  October  26.”  (IR  05000277  &  278/2000-012.)

November  13,  2000 -   “Operators  reduced  load to  79% [at Unit-2] to

repair  the  2C  circulating  water  pump  traveling  screen.  The  unit  was  restored  to

10%  power  on  the  same  day.”  (IR  05000277  &  278/2000-012.)

December  17,  2000 - An  LER  was  issued  “when  a  lightning  strike  caused

the  failure  of  a  communications  circuit  board to  a main  off  gas  stack  radiation

monitor  which  resulted  in  a  spurious  invalid  signal  causing  the  isolation.” Unit  3  was  at  approximately  18%  power  when  the  lightning  strike  caused

the  isolation.  (IR  05000277&278/2001-002).

March  23,  2001 -  Examinations  for  reactor  operators  and  senior  reactor

operators  held  from  February  5-12,  2001,“indicated  that  a  relatively  high

percentage  of the  applicants  were  not  well  prepared  for the  exam.” (Richard  J.

Conte,  NRC,  Chief,  Operations  Safety  Branch,  Division  of  Reactor  Safety.)

May  20,  2001-   Corbin A. McNeill’s  base  salary  after the merger

increased  from  $659,857 to  $855,830  and  his  bonus  was  increased  from  $1

million  to  $1,081,  4572. In  addition, McNeill's  restricted  stock  increased  from

$942,188 to  $2.8 million.   (See  June  13  and  September  28,  October  24  &

December  21,   2001,  for  information  on  900  job  cuts,  and  refer  to  January  29,

2002,  for  further  job  cuts.  Also,  reference  February  26,  2002,  for  information

on  McNeill’s  “retirement  package.”)

May  29,  2001 - At  Unit  3,  “... the fifth  stage feed  water  heaters  were

removed from  service for  end-of-cycle  coast  down. Unit  3  ended the  inspection

period  at  approximately  98  percent  power  with  the  four  stage  feedwater  heaters

removed  from  service.”  (IR  50-277/01-05,  50-278/01-05  &  07201027/01-05).

June  13,  2001 -  Exelon  Nuclear  “announced  its  intent  today  to  eliminate

292  Local  15  Union  positions,  including  138  layoffs  in  Exelon  Nuclear  and  154  at

Commonwealth  Edison.”  (Exelon,  New  Release,  June  13,  2001.)  (See  September

3,  1998,  for  further  Exelon  “downsizing”). (Refer  to May  20,  2001,  for  Corbin  A.

McNeill’s  pay  raise.)

June  22,  2001-  After  widespread  public  criticism,  AmerGen  “notified  the

Nuclear  Regulatory  Commission  that  it  intends  to  delay  submitting  its

application  seeking  approval  for  a  standardized  emergency  plan  for  Three Mile

Island,  Peach  Bottom  and  Limerick.” (Exelon  Nuclear,  Press  Release,  June  22,

2001.)  (See  August  15,  2001  for  more  information  &  November  7,  2001,  for  a

related  development)

June  30,  2001 - At  Unit  2,   “...operators  commenced  an  unplanned

power  reduction  to  approximately  63  percent  to  allow  repair  of  an  electrohydraulic  control  system  leak  at  a  servo  on  the  No.  2 main  turbine  control

valve.  Later  that  same  day,  operators  returned  the  unit  to  100  percent  power.”

(IR  50-277/01-05,  50-278/01-05  &  07201027/01-05).

June  30,  2001  -  “...Exelon  Nuclear  notified  the  Nuclear  Regulatory

Commission (NRC) that it intended to file for  renewal  of the  operating licenses for

Peach  Bottom  Units  2  and  3...

“If  approved,  Unit’  2’s  license  would  be  extended from  2013 to  2033  and

Unit  3’s  from  2014  to  2034...“The  Nuclear  Regulatory  Commission  is  expected to take two  years to

thoroughly  review  the  license  renewal  application  before  determining  whether

to  grant  the  license  extensions...”

“The total  cost  of obtaining the  renewed licenses for Peach Bottom will be

about  $18 million,  including  the  NRC  review,  or  about  $8  per  kilowatt

hour...Exelon Nuclear  also  has notified the NRC that  it  intends to file for  license

renewal[s] for  its  Dresden  and  Quad Cities  Stations  in Illinois.” (Exelon  Nuclear,

Press  Release,  July  2,  2001.)

August,  15,  2001-  The  NRC’s  Office  of Investigation  documented  criminal

behavior  by two  of Exelon’s Emergency  Preparedness  personnel.  The  NRC found

that  the  “technicians  fabricated  siren  testing  maintenance  records,  performed

deficient  siren tests  on the  off  site EP  response  sirens  and intentionally installed

jumper  wires  in  the  siren  boxes  disabling  important  system  functions.”  (Wayne

D.  Lanning,  NRC,  Director  of  Reactor  Safety.) (Refer to August   22,  2001, for

background  information,  and  see  October  23,  2001,  for  penalty  assessment.).

(See   June  22   &  November  7,  2001, for  related  developments.) (See  October  5-9,

2001,  for  a  related  problem  at  TMI.)

August  22,  2001 -  The  NRC  determined  that  a  white  “finding”

(Violation)  was  warranted  for  the  following  infractions  relating  to  the  plants

Public  Address  (PA)  system  and  evacuation  alarm/siren  (EA)  system:

- 1.   From  1992  to  December  19,  2000,  approximately  47%  of  the  PA

system’s  speakers  were  either  inaudible  or  degraded to the  point that  personnel

were  not  able  to  clearly  hear  instructions.

- 2.  From  January  19,  2001  to  February  13,  2001,  and  again  from  March

20,  2001  to  April  17,  2001,  the  plant  PA  system  was  operated  only  on  the

backup  power  breaker,  which  would  have tripped  after  about  49  seconds  of

evacuation  alarm  actuation  on  the  first  sequence.  (The  primary  breaker  had

tripped  following  the  monthly  test  the  beginning  of  each  period.)

- 3.  On  February  13  and  April  17,  2001,  the  plant  PA/EA  system  would  not

properly  function  in  that  both  the  primary  and  the  backup  breakers  were

tripped for  periods  of  4.5  hours  and  1.5  hours  resulting  in  no  system  capability to

provide  instruction  or  sound  the  evacuation  alarm.  (Hubert  J.  Miller,  NRC.

Regional  Administrator.)  (See  August,  15,  2001,  for  a  related  development.)

August  20,  2001 -  “...the  inspectors  observed  a  health  physics

technician  that  was  inattentive  to  his  duties  when  he  was  assigned  to  restrict

access to  a  posted  high  radiation  area  on the Unit  3 turbine floor...that  applies to

high  radiation  areas  with  dose  rates  in  excess  of  100 millirem  per  hour  but  less

than  1000  millirem  per  hour  at  30  centimeters  from  the  source...”  (IR  50-

2 7 7 / 0 1 - 0 9 ,   5 0 - 2 7 8 / 0 1 - 0 9 ) .This was the nineteenth  Non-Cited  Violation since  June  1998.

September  6,  2001 - A  Non-Cited Violation  “of  very  low  safety

significance” was  recorded for,  “The failure to test the Units  2  and  3 HPCI [high

pressure  coolant  injection] torus  suction  check  valves  for  seat  leakage  in the

reverse  flow  direction  was more than minor  because  it  had  a  credible  impact  on

safety.  Significant  leakage  in  the  reverse  flow  direction  could  prevent  HPCI  from

performing  its function  when HPCI  is  aligned to  pump  water from the torus. The

failure  to  leak  test  these  valves  affected  the  Mitigating  System  cornerstone  since

HPCI  performs  an  accident  mitigation  function.”  (IR  50-277/01-06,  50-278/01-

0 6 ) .

This was the twentieth Non-Cited  Violation since  June  1998.

September  8,  2001-  Unit  2  was taken  critical  and  “operated  at

approximately  100%  power  for the  remainder  of the  inspection  period  except  for

scheduled  power  changes  to  support  rod  pattern  adjustments.”   (IR  50-277/01-

09,   50-278/01 -09) .

September  14,  2001-  Unit  3   “began this  inspection  period  at

approximately  81  percent  power,  in  end-of-cycle  coastdown,  with  the  fourth  and

fifth  stage  feedwater  heaters  removed  from  service  on.  On  September  14,  2001,

Unit  3  was  manually  scrammed,  in  preparation  for  the  3R13  refueling  outage.

Unit  3  ended the  inspection  shutdown  in Mode  5 (Refueling).”   (IR  50-277/01-09,

5 0 - 2 7 8 / 0 1 - 0 9 ) .

September  17,  2001-  TMI-Alert  filed  a  Petition  for  rule making  with the

NRC  requiring  the  Agency  to  mandate  armed  security  guards  at  the  entrance  to

all  nuclear  rower  plants.  A  final  decision  is  expected  in  November  l,  2002.  The

Nuclear  Energy  Institute,  Exelon’s  s  “voice  in  Washington,  “recommended”  that

the  Petition  be  “denied.”

September  28,  2001 - With third  quarter  profit  projections  down from

$1.35 to  $1.80  a  share, Exelon  announced the  elimination  of  450  jobs. (See  June

13,  2001,  for  earlier  job  losses.)

Exelon’s  stock  dropped to $44.50  on  September  27,  2001. (See May  20,

2001,  for  Corbin  A. McNeill’s  pay  raise,  and  October  24,  December  21,  2001,  for

related  downgrades.)

October  1,  2001 - The NRC  reported  on Exelon's Emergency Preparedness

p r o g r a m :

Although  you  believe  the  current  EP  program  remains  ready  to  effectively

protect  public  health  and  safety,  you  stated  it  did  not meet Exelon’s  vision  of  an

industry  leading  program.  Your  presentation  included  changes  and

improvements  to: (1)  EP  organization/staffing; (2)  EP  equipment  reliability; (3)

EP  program  processes;  and  94) the  corrective  action  process. (Richard  J. Conte,

Chief,  NRC,  Operations  Safety  Branch,  Division  of  Reactor  safety,  October  18,

2001.  (See   June  22   August  15,  2001  for  background  information  &  November

7,  2001,  for  a  related  development)

October  5-9, 2001 -   At TMI,  “Licensee  sirens in Lancaster County were

inoperable  October   5 through  October  9,  2001,  due to  a  radio transmitter  being

deenergized  at  the  county  facility.  The  transmitter  is  part  of  the  siren  actuation

system.  This  issue  is  unresolved  pending  further  investigation  into the  lines  of

ownership  and  maintenance  of  the  actuation  system”  (IR  50-289/01-07.)  (See

August  15,  2001,  for  a  related  problem  at  Peach  Bottom.)

October  6,  2001 -  The  Federal Energy  Regulatory Commission (FERC)

filed  a  “show  cause”  order  relating to  PECO  Power Team’s  purchase  during  a

power  auction  that  may  have  benefited  from  “informational  advantage”  from

Peco.  (“Philadelphia  Inquirer”,  October  6,  2001.)  On  December  19,  2001,

according  to  Exelon,  the  FERC  “terminated  its  investigation  into  alleged

wrongdoing...”  (Exelon  Corporation,  Press  Release,  December  19,  2001.)

October  6,  2001 -  After  the  September  11,  2001  terrorist  attacks  on  the

World  Trade  Center,  the  Pentagon  and  a  downed  airliner  in  Somerset  County,

Pennsylvania,  the  NRC  has  issued  a  “Security  Advisory”,  and  requited  13

“prompt  actions  which  are  “safeguarded”  and  “classified.”  (See  October  17,  2001

&  November  2,  2001,  for   related  incidents).

October 8,  2001- The NRC issued  another Non-Cited Violation,  and

concluded that Exelon’s  “Troubleshooting,  Rework,  and  Testis  Process” (TRT)

“would  not  adequately  control  Unit  3  reactor  vessel  water  levels.”   (IR  50-

2 7 7 / 0 1 - 0 9 ,   5 0 - 2 7 8 / 0 1 - 0 9 )

This was the twenty-first  Non-Cited  Violation since  June  1998.

October  8,  2001-  Unit  3  was taken  critical  and  “operated  at

approximately  100%  power  for the  remainder  of the  inspection  period  except  for

scheduled  power  changes  to  support  rod  pattern  adjustments.”   (IR  50-277/01-

09,   50-278/01 -09) .   -  October  12,  2001-   “....during  the  Unit  3  startup  from  a  refueling  outage,

when the  jet  pumps  had  been  cleaned,  core flow  exceeded  100% (at  106.3%) for  a

period  of  ninety minutes  before  operations  personnel  initiated  actions to  reduce

core  flow  to  within  100%.”   (IR  50-277/01-07,  50-278/01-07.)

This was the twenty-second  Non-Cited  Violation since  June  1998.

October  17,  2001 -  Due to  a  ”credible threat”  against  Three Mile Island,

the  Harrisburg  and  Lancaster  airports  were  closed  for  four  hours,  air  travel  was

restricted  in  a  20-mile  radius,  a  fighter  jets  were  scrambled  around  TMI. (See

October  6,  2001,  &  November  2,  2001,  for  a  related  events.)

- Through the Freedom  of Information Act, the York Daily  Record

(December  21,  2003)  found  a  “twofold”  challenge  when  a  threat  against  Three

Mile Island  caused the Harrisburg  and Lancaster  airports to  close for four hours:

Air  travel  was  restricted  in  a  20-mile  radius  and  fighter  jets  were  scrambled

around TMI.

Officials struggled with whom to call first, next and last. Officials

struggled  with  notifying  state  and  local  officials.  And  officials

struggled  with  when  and  whether  to  notify  the  public...One  NRC

official  had  difficulty  reaching  senior  management  at  TMI...No

one  contacted  enforcement  officials  in  York  County  about the

threat...[PEMA]  officials  had to  push  plant  officials to  staff their

emergency  operations  facility

[in Susquehanna Township which was later  relocated to Coatesville].

October  19,  2001 -  PSE&G  acquired  Atlantic  City  and  Electric  Company’s

stake  in  Peach  Bottom. (See  December  1,  1999,  for  a  related  acquisition  by

C o n n e c t i v ) .

October  23,  2001 -  On August,  15,  2001, the  NRC’s  Office  of Investigation

documented  criminal  behavior  by  two  of  Exelon’s  Emergency  Preparedness

personnel.

In  accordance  with  the  Enforcement  Policy,  a  base  civil  penalty  in  the

amount  of $55,000 is  considered for  Severity Level III  violation  or  problem.

Because  the  Severity  Level  problem  was  deliberate,  the  NRC  considered  whether

credit was warranted for Identification  and Corrective Action  in accordance with

the  civil  penalty  assessment  process  in  Section  VI.C.2  of the  Enforcement  Policy.

In this  case, the NRC  decided that  credit for Identification  is  warranted  because

you  identified  the misconduct  and  informed  the  NRC.” (Hubert Miller,  NRC,

Regional  Administrator,  October  23,  2001).This was the twenty-third   Non-Cited  Violation since June 1998.

Exelon's total  cost  avoidance, i.e., “credit” for 23 Non-Cited Violations = $1,

155,000.

October  23,  2001 -  At  Unit  2,  “an  automatic  reactor  shutdown  occurred

due  to  a  generator  lockout  and  main  turbine  trip.  Following  troubleshooting  and

repairs, the  unit  was  restarted  on  October  27  and  reached  100%  power  on

October  30.  (IR  50-277/01-09,  50-278/01-09).

October 24, 2001 - Exelon Corporation’s  stock was downgraded from

“Buy”  to  “Mkt  Perform”  by  Banc  of  America  and  from  “Strong  Buy”  to  “Hold”  by

UBS Warbug. (See May  20,  2001,  for  Corbin A. McNeill’s  pay  raise,  and

September  28  and  December  21,  2001,  for  related  downgrades.)

October  30,  2001 -  “...the  E-2  emergency  diesel  generator (EDG) tripped

on  low  jacket  coolant  discharge  presurre  during  routine testing  of the

EDG...Although  Exelon  was  unable  to  detemine  who  closed  this  valve  or  exactly

when  it  was  closed, they  did  determine that the  valve  was  closed  somewhere  in

the  period  between  October  12,  2001  and  Ocotber  30,  2001...The  EDG  was

successfully  tested  and  returned  to  service  on  October  31,  2001”  (IR  50-277/01-

10,   50-278/01 - 10. )

This was the twenty-fourth Non-Cited  Violation since June  1998.

Exelon's total  cost  avoidance, i.e., “credit” for 24 Non-Cited Violations =

$1 ,205,000.

November  2,  2001  -  Governor  Mark  Schweiker  reversed  an  earlier

decision,  and  ordered  the  National  Guard  to  Pennsylvania’s  nuclear  power

plants.The  Commonwealth  joins  over  a  dozen  states  with  National  Guard  and/or

Coast  Guard  detatchments  depolyed  to  protect  nuclear  facilities  against  terrorist

attacks. (See  October  6  &  17,  2001,  for   related  incidents).     - November  7,  2001 - Exelon met with the NRC to discuss the  consolidation

of Emergency Plans for TMI, Peach Bottom  and Limerick.   Exelon  requested the

plans  be  approved  and  implemented  by  January  2,  2002.  The  following

personnel  (17),  including  a  “Security  Coordinator”  would  be  affected:

* LGS and PB Emergency Plan Positions Affected

- 1  Communicator

- 2  Dedicated Maintenance  Technicians

1 Dose Assessor

2 Dedicated Off-Site Survey member

* TMI Emergency Plan Positions Affected

- 4   Technicians

1 On-Site OSC Coordinator

1 Dose Assessor

1 Off-Site Field Team  Member

- 1  Communicator

1Security  Coordinator

- 2  Auxiliary  Operators.

(Presentation  by: William  Jefferson,  Director,  Generation  Support,  Exelon

Nuclear,  MidAtlantic  Regional  Operating  Group,  May  16,  2001.)  (See   June  22,

August  15,  &  October  1  2001,  for  related  developments.)

November  8,  2001 - At  Unit  3,   “...operators  commenced  a  schedlued

power  reduction  to  approximatley  19%   because  a  primary  containment

isiolation  valve  in  the  redisual  heat  removal  system  in  the  drywell  failed  to  close

when  it  was  tested.”(IR  50-277/01-10,  50-278/01-10.)-November  28,  2001 -Exelon  Power  Team  stated  that  the

collapse  of  Enron  will  cost the  Company  “less than  $10 million.  The

current  direct  exposure  (i.e.,  for  current  energy  sales  from  Exelon  to

Enron) is less than $20 million. (Exelon  Corporation,  Press  Release,

November  28,  2001.)(See  October  8,  1997,  for  a  related  development.)

- Three  days  later,  on  December  1,  2001,  PPL  stated  that  the

collapse  of  Enron may  cost the  Company  $40 million  for  energy

already  purchased. Enron  also  owns  45%  of  power  plant  in New

- England operated by PPL. (Philadelphia Inquirer, Business, December

1,  2001.)

November  30,  2001 - At  Unit  2,   “...operators  commenced  a  schedlued

power  reduction  to  approximatley  19%  to  repair  an  instrument  nitrogen  leak  in

the  drywell.  Following   repairs,  the  unit  power  was  increased  and  reached  100%

on  Decmber  2,  2001.”

(IR  50-277/01-10,  50-278/01-10.)

December 5, 2001 - Business Day  of  Joahnnesburg  South Africa  reported

Exelon was negotiating to but 40 Pebble Bed Modular Reactors from Eskom. The

order,  estimated to  be  as much  as $6  billion,  assumes  delivery  of the  reactors to

the  Untied  States  by  2007.  (See  December  10,  2001,  for  related  development.)

Refer to April  17,  2002, for  information  realting to Exelon’s  decision to

pull-out  of the  project.

December  10,  2001 -  Unreco,  a  uranium  supplier,  is  seeking  regulatory

approval  to  build  the  first  new  enrichment  facility  in  the  US  in  half  a  century.

The project,  estimated to  cost $10, is  a joint  venture  of Exelon  and duke Power.

(Financial  Times, December  10, 2001) (See December 5, 2001, for  a   related

d e v e l o pme n t . )

December  21,  2001- Exelon  Corporation’s  stock  was  downgraded  from

“Accumulate”  to  “Hold”  by  Jeffries  &  Co.,  and  Lehman  Brothers  stated,  “We

believe  an  economic  recovery  is  key  to  the  Exelon  story,  which  is  highly

leveraged  to  power  prices...”  (Reuters,  December  21,  2001.)  (See  May  20,  2001,

for Corbin A. McNeill’s  pay  raise,  and  September  28  and  October  24,   2001, for

related  downgrades.  Also,  refer  to  January  29,  2002,  for  further  job  cuts.)

January  9,  2002  -  A  well-armed,  disgruntled  former  employee  at  the

San  Onfore  nuclear  power  plant  in  San  Clemente  was  arrested  for  making

threats  against  the  plant.-  January  11,  2002 -  Siren  testing  at  TMI  ecountered  numerous  problems:

all  sirens failed  in  York County  and  one  siren failed  in  Lancaster County.

AmerGen  attributed  to  computer  malfucntions.  (August,  15,  2001,  and  October

5-9,  2001.)

January  9,  2002  -  A  well-armed,  disgruntled  former  employee  at  the

San  Onfore  nuclear  power  plant  in  San  Clemente  was  arrested  for  making

threats  against  the  plant.  (See  October,  6,  2001,  and  January  30  and  December

10,  2002,  for   related  incidents.)

- January  11,  2002  -  Siren  testing  at  TMI  encountered  numerous

problems:  all  sirens failed  in York County  and  one  siren failed  in Lancaster

County.  AmerGen  attributed  to  computer  malfunctions.  (August,  15,  2001,  and

October  5-9,  2001.)

January  29,  2002 - Exelon  announced  it  would  cut  3,400  or  15%  of  its

work force  by the  end  of  2002. (See May  20,  2001, for Corbin A. McNeill’s  pay

raise,  June  13  and  September  28,  October  24  &  December  21,   2001,  for

information  on  900  job  cuts.  Also,  reference  February  26,  2002,  for  information

on  McNeill’s  “retirement  package.”)

- January  30,  2002 - President Bush’s  State  of the Union Address

including  a  warning  that  nuclear  power  plants  may  be  targeted  for  a  terrorist

attack.  (See  October  6  &  17  and  November  7,  2001,   and  January  9,  2002  for

related  events.)

February  14,  2002   -  Exelon  prepared  an  “inadequate  critique”  of  their

“emergency  preparedness  exercise.”  (See  July  1,  2002.)

February  26,  2002 -  Corbin McNeill  Jr.  announced  his  retirement,  and

he  is  expected to  receive  $7 million  when  leaves the  Company  in  April,  2002.  He

will  also  receive  a  bonus  payment.  McNeill  made  $2.5  million  in  2001.*

“His  severance  equals triple the  sum  of  his  annual  base  salary  plus the

average  of  his  bonus  over the  last  two  years.

“McNeill  is  the  company’s  largest  individual  shareholder.  His  1.53  million

shares  are  worth  $79.1  million  based  on  yesterday’s  closing  price  of  $51.70.”

(Philadelphia  Inquirer, C-1, March  14, 2002.)*  Corbin A. McNeill’s  base  salary,  after the merger  increased,  from

$659,857 to  $855,830,   and  his  bonus  was  increased from  $1 million to

$1,081,572.  In  addition,  McNeill's  restricted  stock  increased  from  $942,188  to

$2.8  million.  [May  20,  2001.]

(See  June  13  and  September  28,  October  24  &  December  21,   2001, for

information  on  900  job  cuts,  and  refer  to  January  29,  2002,  for  further  job

cuts.  ”)

March  28, 2002   - The NRC  admitted that Peach Bottom   and the  102

nuclear  power  plants  could  not  withstand  an  impact  of  airplane the  size  of those

that  crashed  into  the  Pentagon  and World  Trade  Center  on  September  11,  2001.

(March  28,   2002, Patriot  News.) (See  October  2001  &  October  17,  2001  and

January,  9  and  30,   2002,   for  related  incidents.)

April 3, 2002   -   “Two men and a male juvenile from Mexico face possible

deportation  after  attempting  to  enter  an  unprotected  area  of  the  Peach  Bottom

Atomic  Power  Station.  All  three  remained  in INS  custody  Wednesday.”(York

Daily  Record, April  4,  2002.) (See  January,  2001,  October  6,  2001  &  October

17,  January,  9  and  30,   2002,   and  March  21  and  May  15,   2002,  for  related

inc ident s . )

April  17,  2002 -   Exelon  Corp.,  the  country's  largest  nuclear  plant

operator,  said  yesterday that  it  would  end  its  bid to  develop the  next  generation

of  nuclear  reactors.

The Chicago-based  parent  of Peco Energy Co.  said  it would terminate  its

nearly  two-year  relationship  with  Eskom,  South  Africa's  state-owned  utility,  in

building  a prototype  gas-cooled  reactor. Exelon is  getting  out  of the business  of

designing  nuclear  plants  and  will  concentrate  instead  on  operating  them.

The  company  spent  $20 million  on the  project,  of  which  it  owned  12.5

percent. Exelon  said  it  already  had  paid for  its  share  as  a  research-anddevelopment  expense. It has not  decided what to  do with the  12  employees  it  had

working on the project, a  spokeswoman  said. (Benjamin Y. Lowe, Philadelphia

Inqui r e r,   April  17, 2002.) (See  December   5  &  10,  2001, for  background

i n f o rma t i o n . )

- April 22, 2002 - Exelon's 1st-Quarter Net Income Fell 98%

...  as  mild  winter  weather  and  maintenance  costs  hurt  results.

“The  country's  largest  operator  of  nuclear  power  plants  reported  late

Monday net income  of $8 million,  or two  cents  a  share,  compared with net

income  of  $399  million,  or  $1.23  a  share,  a  year  earlier.

“The  latest  results  included  a  charge  of  $230 million,  or  71  cents  a  share,

from the  effect  of  adopting  SFAS  142  for  goodwill  amortization,  while  year-

earlier  results  included  a tax  benefit  for the  implementation  of  SFAS  143  for

derivatives.  Excluding  these  items,  the  company  said  it  had  operating  earnings

of  77  cents  a  share,  compared  with  operating  earnings  of  $387  million,  or  $1.19

a share.” (Mon Apr 22,10:53 PM ET , CHICAGO -- Exelon Corp. )

(See  June  13  and  September  28,  October  24  &  December  21,   2001; and,

January  29  &  February  26,  2002.  For  information  related  economic

de v e lopment s . )

May  11,  2002-  “Exelon Corp.  is the  subject  of  a  shareholder   lawsuit

alleging  the  electric  and  gas  utility  made  false  and  misleading  statements  that

artificially  inflated  its  share  price.  The  law firm  of  Charles  J.  Piven  said  it filed  a

lawsuit  on  behalf  of  buyers  of  Exelon  shares  between April  24,  2001,  and

September  27.”   (Philadelphia  Inquirer, D-3, May  11, 2002.)

May  15,  2002  -  “A  foreign  intelligence  service  recently  warned  that  a

nuclear  power  plant  in the  Northeast  could  be the target  of  a  July  4 terrorist

attack...Published  reports  suggested  that  the  target  could  be  Pennsylvania’s

Three Mile Island, but  a  second US official with  knowledge  of the information  said

no  specific  facility  had  been  named.” (Knight  Ridder, May  15,  2002.) (See

January,  2001,  October  6,  2001  &  October  17,  January,  9  and  30,   2002,   and

March  21,  for  related  incidents.)

May  28,  2002 -  “Exelon Corp.  and three  other  utilities [Main  Yankee

Atomic  Power  Co.,  Omaha  Public  Power  District  &  Sacramento  Municipal  Utility

District]  lost  a  $2.2  billion  legal  challenge  to  the  federal  government’s  nuclearwaste  cleanup  plan...In  1992,  Congress  ordered  utility  companies  that  use

government  uranium-enrichment  services  to  pay  one-third  of  the  cleanup  bill.

The  U.S.  Supreme  Court  said  yesterday that  it  would  not  hear  an  appeals  from

the  companies  that  argue  that  the  assessments  are  unconstitutional.”

(“Associated  Press”,  May  29,  2002.)

June  2,  2002 -An  alert  began  at  around  12:30  am,  ending  at  3:01  am,

relating to the  activation  of the  fire  suppression  system  due to EDG  failure  which

released  carbon  dioxide  into  a  room  where two  employees  were  working. No

injuries  were  reported  and  both  Peach Bottom  2  &  3  remained  at  100%  power.

(Exelon  Nuclear,  News  Release,  June  2,  2002,  4:10  am.)  (See  November  26,

2002  for  follow-up,  and  July  11,  2003  for  absolution.)

June  12,  2002 -  The Bioterrorism Bill  signed  into  law  on  June  12,  2002

mandates KI  stockpiles  out to 20 miles.

June  25,  2002  -  “...station  emergency  preparedness  personnel  discovered

that  the  emergency  planning  siren  base  station  at  the  site,  was  unable  to

communicate  with the  off  site  sirens,  due to  external  radio  frequency  noise  in the

area.”   (IR-50-277/02-05; 50-278/02-05)

July  1,  2002   - The NRC found that  on  February  12,  2002,   Exelon  “did

not  identify  that  key  information  needed  by  the  emergency  director  (ED)  to

classify the  simulated  event  as  a  General  Emergency  was  not  provided to the  ED

by members  of the Emergency  Response  Organization (ERO).  The finding   was

preliminary  classified  as White  because the  critique  failed to   identify   a  problem

associated  with  the  implementation  of  a  risk  significant  planning  standard.”

...Continued on the following page...Exelon  disputed  the  findings  on  September  4,  2002.

The  NRC  reasserted  that  “the  critique  problems  were  more  than  minor  but

the Issuance  of the White finding  is  not  appropriate  because the  inadequate

critique  did  not  result  in  a  failure  to  identify  a  risk  significant  planning  standard

(RSPS)  problem.”

The incident is  classified  a Non-Cited Violation.

(Final  Significance  Determination  for  Green  and White  Findings  and  a  Notice

of  Violation  at  Peach  Bottom,  IR-50-277/02-07; 50-278/02-07).

This was the twenty-fifth Non-Cited  Violation since June  1998. Exelon's

total  cost  avoidance, i.e., “credit” for 25 Non-Cited Violations = $1 ,255,000.

July  21,  2002-   At  Unit-2,  “the  fifth  stage  feed  water  heaters  were

removed  from  service  for  end-of-cycle  coast  down.”  (IR-50-277/02-05;  50-

278/02-05).  (See  August  4,  2002  for  related  event.)

July  23,  2002-   “Exelon  did  not  evaluate  in  a  prompt  manner  whether  it

was  appropriate to disable the  electrical trips  of the EDGs from the  cardox

injection  fire  protections  system  after  NRC  inspectors  identified that the trips

were  still  active  with  the  EDG  cardox  system  isolated”  (IR-50-277/03-02; 50-

278/03-02)  (Also  refer  to  IR-50-277/02-04; 50-278/02-04).

(See  April  23,  2004  for  NCV).

August  4,  2002-   At  Unit-2,  “the fourth  stage feed  water  heaters  were

removed  from  service.”  (IR-50-277/02-05;  50-278/02-05).  (See  July  21,  2002

for  related  event.)

August  15, 2002 - Despite a favorable EIS of Exelon’s  request for a license

extension  at Peach Bottom-2 & -3, the NRC listed three  safety issues that need to

be  addressed  prior to  approval:  replacement  o  electric fuse  clips;  removal  of the

anti-aging  plan;  and,  replacement  of  faulty  cables.

August  30,  2002-   At  Unit-3,  “power  was  reduced to  approximately  90%

prior to  shut  down the  3  ‘A’  recirculating  water  pump  because  of  high

differential  pressures  on  the  circulating  water  intake  screens.  The  high

differential  pressures  were  caused  by  a  sudden  surge  in the  amount  of fish

(Gizzard  Shad) that  entered the  intake  canal  and  clogged the  screens.  Unit  3

power  was  returned  to  100  percent  following  cleaning  of  the  circulating  water

screens  and  restating  of  the  3’A’  circulating  water  pump.”   (IR-50-277/02-05;

50-278/02-05).

- August  31,  2002 -  New  security  budget  increased  to  $2.2  million

annually  or  $550,300  less  than  John W.  Rowe’s  base  salary.- September 5, 2002    -- Three Mile Island Alert filed a formal Petition for

Rulemaking  with  the  Nuclear  Regulatory  Commission  to  include  day-care

centers  and  nursery  schools  in  emergency  evacuation  planning.  The  proposed

rule  would  affect  all  103  operating   nuclear  plants  in  the  United  States.

September  10,  2002 -  The  Office  of  Homeland  Security  announced that

the   “yellow”  warning  had  been  increased to  a  heightened  state  of  alert   or  an

“orange”  upgrade  at  1:00  pm.   (Exelon  Public  Relations.)

-  “...Unit  2  was  manually  scrammed,  in  preparation  for  the  2R14

refueling  outage”  (IR-50-277/02-05; 50-278/02-05).

November,  2002 -  “  Governor  Schweiker  “directed  the  National  Guard  to

join  State  Police  in  a  joint  security mission  at the  state’s  nuclear facilities.” In

December, the  Governor  extended the  joint mission  of the  National  Guard  and

the  State  Police  at  the  Commonwealth’s  five  nuclear  generating  stations  until

March  4,  2002.  (DEP, Update,  December  6,  2002.)

- September  21, 2002 - A Non Cited Violation was issued for incident

“when  a  chain  broke”  on  a  “rigging  hoist  and  the  motor,  weighing

approximately  48,000  pounds,  fell  approximately  ten  inches  into  the

pump/motor  stand.”

This was the twenty-sixth Non-Cited  Violation since June  1998. Exelon's

total  cost  avoidance, i.e., “credit” for 26 Non-Cited Violations = $1 ,355,000.

November  26,  2002 - Initially  classified  as  a White, the incident  was

classified  a  Non-Cited  Violation.  (See  June  2,  2002, for  precursor  event.)

(Final  Significance  Determination  for  Green  and White  Findings  and  a  Notice  of

Violation  at  Peach  Bottom,  IR-50-277/02-07;  50-278/02-07).

This was the twenty-seventh Non-Cited  Violation since June  1998.

Exelon's total  cost  avoidance, i.e., “credit” for 27 Non-Cited Violations =

$1 ,355,000.

December  10,  2002 -  A  security  challenge  occurred  at  an  Exelon  nuclear

power plant  outside  of Chicago.

“BRAIDWOOD --  A  crazed  Chicagoan,  swearing to  be  an  extraterrestrial

alien,  crashed  his  car  through  the  gates  of  the  Braidwood  nuclear  facility  late

Monday  before  speeding  away  only to  be  arrested for  reckless  driving  in

Wilmington  minutes  later.

...Continued on the following page...   No  injuries  resulted. Metta  said the  intruder  is  alleged to  have

penetrated  the  parking  area  by  crashing  through  closed  gates,  flashing  past  a

plant  checkpoint  and then  doing  "donuts"  in the  parking  lot. (“The  Daily

Journal”,  Kankakee  IL.)” (See   January  9  and  December  20,  2002,   for  related

inc ident s . )

December  12,  2002 - TMI  sirens malfunctioned  in Cumberland   and York

counties.  In  Dauphin  County,  28  sirens  malfunctioned  due  to  the  “inadvertent”

discharge  of the  “space  bar”  by  a  computer  operator. (Refer to  June  22, August

15   and  October  5-9,  2001  and  January  11,  March  3  2002,  for  related

problems.)

December  20,  2002 - Another   security  challenge  occurred  at  an  Exelon

nuclear  power  plant  outside  of  Chicago:

“BRAIDWOOD -- She was the  second driver to breeze past the guard  station

at  Braidwood’s  nuclear  facility  in the  span  of  a  week.

“But  its  unclear  if  the  trespasses  arrest  of Wilmington’s  Christina  Staley,

Tuesday,  will  result  in  changes  to  the  nuclear  generating  station’s  security

apparatus.

“Neal  Miller,  station  director,   noted  that  Ms.  Staley,  31,  had  apparently

become disoriented  and was looking for  some place to turn  around when  she

drove  past  the  security  at  9  a.m.”

(“The  Daily  Journal”,  Kankakee  IL.)”

(See   January  9  and  December  10,   2002,   for  related  incidents.)

December  13,  2002  -  A  security  challenge  occurred  at  a  nuclear  facility

north  of  Peach  Bottom,  on  the  Susquehanna  River

"At  1450 EST  on  12/13/2002,  Susquehanna  LLC Main  Control  Room

received  a  request  for  additional  information  from  the  Pennsylvania  Emergency

Management  Agency  (PEMA).  PEMA  received  rumors  that  a  HAZMAT  team  had

been   dispatched to Susquehanna in  response to  a  spill  associated with  a potential

sabotage event.

December  17,  2002 -  “...Unit  2  power  was  reduced  to  approximately  16

percent to  facilitate  leak  repairs  on the  Caldon  LEFM  flow measurement  system.

After  repairs,  Unit  2  returned to  100  percent  power  in the  afternoon  of  December

21”  (IR  50-277/02-06;  50-278/02-06).  (See  April   30  -  May  11,  2003,  for  a

similar  problem).

December  21,  2002 -  An  LER  was  recorded  after  “Unit  2  automatically

shutdown  from  100%  power  when the main  steam  isolation  valves  closed  due to

a  Group I  Primary  Containment Isolation  System  (PCIC)  actuation”  (IR  50-277-

03-02;  IR-50-278/03-02). “For  example,  on  Dec.  21,  2002,  a  Peach  Bottom Atomic  Power  Station Unit  2  electro-hydrolic  control  system  circuit  card  failure  triggered  a  scram, according to the  NRC’s  report.  That  system  controls the  wide-range  speed  control of  the  turbine, Sheehan  said.“In  other  words,”  Sheehan  said,  “it  serves  as  a  sort  of  high-tech throttle for the  plant’s  turbine,  thereby  controlling  the  plant’s  power  output.”“On  Dec.  22,  2004, the  NRC  report  said,  another  part  of that  same  system malfunctioned,  causing  a  loss  of  reactor  pressure  and  forcing  a  scram.” (“York Sunday  News”,  March  13,  2005)

January  28,  2003 - An  NCV  was  issued  relating to Exelon's failure to

correct  and  maintain  “preventative  maintenance  activities  and  procedures  on

critical,  safety  related  ventilation  dampers  since  1988...A  contributing  cause  to

the  length  of time that Exelon  did not identify this issue was  related to the

Problem Identification  and  Resolution  crosscutting  area.  Peach  Bottom  plant

personnel  did  not  identify  the  lack  of  preventative  maintenance  for  safetyrelated  dampers  following  the  identification  of  excessive  stroke  times...in  June

2000  or...failure  to  stroke  on  June  16,  2002”  (IR  50-277-02-06;  IR-50-278/02-

0 6 ) .

This was the twenty-eighth  Non-Cited  Violation since June  1998.

Exelon's total  cost  avoidance, i.e., “credit” for 28 Non-Cited Violations =

$1 ,405,000.

February  11,  2003   - A  Severity  Level IV  violation  was  issued  by the

NRC.  Exelon  made  changes  to  their  emergency  plans  without  prior  NRC

a p p r o v a l .

“The  finding  was  determined to  be more than minor  as  its  significance  was

related to the  impact  it  would  have  on the mobilization  of the  emergency

response  organization  and  preclude  offsite  agencies  from  being  aware  of  adverse

conditions  on  site”  (NCV  50-277;  IR-50-278/03-006-01);

This  Violation was  classified  a Non-Cited Violation. This was the twentyninth  Non-Cited  Violation since June  1998. Exelon's total  cost  avoidance,

i.e.,  “credi t” for  29 Non-Cited Violations = $1 ,455,000.

February  17, 2003 -   PEACH BOTTOM-2 WAS REDUCED TO 45%

POWER AFTER A RECIRCULATION PUMP tripped. Exelon spokesman Dave

Simon  said the trip  occurred Feb.  17  at  6:48  a.m. The  root  cause  of the trip  has

not  yet been   determined, he  added. Simon declined to  say how long the unit is

expected to  be  operating  at the  reduced  power  level. Peach Bottom-2  was  at full

power  prior to  incident (Reut e r s.) The plant  ramped up to full power  by February

- 20,  2003. Reuters: Exelon's Pa. Peach Bottom 2 nuke drops to 41 pct

Tuesday  February  18,  8:25  am  ET NEW  YORK,  Feb.  18 (Reuters) -  Exelon  Nuclear's  1,110 megawatt   Peach Bottom  2  nuclear  unit  in  Pennsylvania  was  at  41  percent   power  early  Tuesday, down from full  power  on  Friday, the  U.S.   Nuclear  Regulatory  Commission  said in  its  power  reactor  status   report. It  was  not immediately  known  why  the  unit,  located  in  Delta, Pennsylvania,  had  been  reduced. Meanwhile, the  adjacent  1,110 MW  Unit  3  continued to  operate  at   full

power  on Monday. The NRC did not issue a  reactor  status  report on Monday due to   the U.S. Presidents  Day  holiday. Exelon Nuclear is a unit of Exelon Corp. of Chicago.

April  12-15,  2003  -  At  Unit-2,  “an  automatic  reactor  shutdown  occurred

due to  high  reactor  pressure  after the  ‘D’  outboard main  steam  isolation  valve

(MSIV)  collapsed.   The MSIV  closes  as  a  result of  a failed instrument line  valve.

Unit  2  returned  to  100%  power  on  April  15,  2003”. On  April  12,  2003,  “Unit  2  unexpectedly  shut  down  when  a  single  main steam  isolation  valve failed to  close,  based  on  a  broken  air-supply  line. Exelon concluded  that  the  valve’s  air  tubing  was  vulnerable  to  a  fatigue  failure.“While  the  plant  did  inspect more  than  200  pneumatic  lines  linked  to  airoperated  valves  on  both  Unit  2  and  Unit  3, the  review  did  not take  into  account similar  equipment  such  as  instrument  lines,  according  to  the  report”  (“York Sunday  News”,  March  13,  2005.)- April  19,  2003 - A  Green Non-Cited Violation  was  issued  “when approximately  25  minutes  into  a  planned  load  endurance  test  run  for  the  E2 EDG,  a  small fire  occurred  on the EDG manifold” (IR  50-277-200-3003; IR-50-278/200-3003).  This  was  the thirtieth Non-Cited  Violation since June  1998. Exelon's total  cost  avoidance, i.e., “credit” for 30 Non-Cited Violations = $ 1 , 505 ,000.

April 23, 2003 - A Non-Cited Violation was issued for problems  associated

with  the   EDG  cardox  system  on  July  23,  2002.

This was the thirty-first Non-Cited  Violation since June  1998. Exelon's

total  cost  avoidance, i.e., “credi t” for 31 Non-Cited Violations = $1 ,555,000.

April 23, 2003 - A Non-Cited Violation was issued for problems  associated

with  emergency  lighting  units  from  November  6,  2002  through  March  30,

2003.  Eight-hour  support  batteries  for  three  areas  were  not  provided,  i.e.  Unit  2

RHR  room, Unit 3 RHR  room  and Unit 3 RB  “south isolation  valve  room.”

(IR  50-277-03-02; IR-50-278/03-02).

This was the thirty-second Non-Cited  Violation since June  1998.

Exelon's total  cost  avoidance, i.e., “credit” for 32 Non-Cited Violations =

$1,610,000.

April   30 - May  11,  2003 -   Unit-2  power  “was  reduced to  approximately

30  percent to facilitate  repairs to the Caldon  leading  edge flow meter (LEFM)

system  and  for  power  suppression  testing,  to  identify  a  leaking  fuel  assembly.

During  power  ascension  to  approximately  85  percent,  on May  6,   following

repairs to the Caldon LEFM  system  and  after the  leaking fuel  assembly  was

identified  and the  adjacent  control  rod  was  inserted  and  de-energized, the #3

main  turbine  control  valve  started  oscillating.  Unit  power  was  reduced  to

approximately  40  percent  to  facilitate  repairs  to  the  main  turbine  control  valve.

On May  11,  2003,  Unit  2  returned  to  10o  percent  power  after  the  #3  main

turbine  control  valve  was  repaired”  (IR  50-277-200-3003;  IR-50-278/200-

3003).  (See  December  17,  2002,  for  a  similar  problem).

May 8, 2003 --The NRC RENEWED THE OPERATING LICENSES FOR

PEACH BOTTOM-2 AND -3  FOR AN  additional  20  years, the  agency  said today.

The  licenses  will  now  expire  on August  8,  2033 for  unit  2  and  July  2,  2034  for

unit  3.  Exelon  had  submitted  the  license  renewal  application  on  July  2,  2001

(Platts, Nuclear News.)

May 8, 2003 --EXELON LOWERED POWER AT PEACH BOTTOM-2 TO FIX

A TURBINE CONTROL VALVE. The problem was discovered  at  around  3 p.m.

yesterday  as the  unit  was  powering  back  up  following  completion  of  power

suppression  testing,  company  spokesman  Dave  Simon  said.  The  unit  had  been

operating  at  around  61%  since  April  30  while  the  power  suppression  testing  was

being  conducted. It  reached  as high  as 86% before  being lowered to 42% to  repair

the  control  valve.  Simon  declined to  say  how  long the  repairs  would take  or  when

the unit would be  returned to full power (Platts,  Nuclear  News. )

May  13,  2003 -  During  a  surveillance  test,  technician  discovered  a  “  wire

for  the  station  power  supply”  was  broken.  (IR  50-277-03-02;  IR-50-278/03-02).

This was the thirty-third   Non-Cited  Violation since June 1998. Exelon's

total  cost  avoidance, i.e., “credit” for 33 Non-Cited Violations =

$1,665,000.

- SCRAM:  APPENDIX "R" ISSUE AT PEACH BOTTOM 3

-  "On  May  14,  2003,  at  approximately  0410,  the  shift  supervisor

determined  that  the  Alternate  Shutdown  Panel  on  Unit  3  was  not  operable

following  discovery  of  a  de-energized  power  supply.  The  panel  provides the

capability   to maintain  a  safe  shutdown  path for  a fire  in the  cable  spreading

room, main  control  room  or main  control  room fan  room.  Therefore,  operators

would   have  been  prevented  from  implementing  required  actions  for  a  fire  in

those    areas. The apparent  cause of the loss of power was a broken wire, which

was  discovered during routine testing of the panel.

"Power  was  restored  to  the  Alternate  Shutdown  Panel  at  approximately

1030  on  May  14,  2003  and  further  investigation  is  in  progress  to  determine  the

cause of the broken wire  and full  extent  and  effect of the de-energization of the

panel."          (U.S. Nuclear Regulatory Commission Operations Center,

Event  Reports  For  05/14/2003  -  05/15/2003.)

“Pa. Nuclear Operator Found Drunk on Job”

May  14,  2003  -  An  employee  at  two  Pennsylvania  nuclear  power  plants

has  been  suspended for  being intoxicated  on the job,  according to  a Nuclear

Regulatory  Commission  report. The  employee tested  positive  as  being  under the  influence  of  alcohol  during a  random  May  14  drug  test  at  the  Limerick  Generating  Station,  according  to  the report.  The  test  was  given  at  9:45  a.m.,  when  the  employee  had  already  been  at work  for  several  hours,  the  report  stated.

...Continued on the following page...The  employee  had  been  licensed to  operate  reactors  at the  Limerick  plant in Montgomery  County  and the  Peach  Bottom  plant  in  York  County  before  being suspended  by  Exelon  Nuclear,  officials  said.

The NRC  considers nuclear workers with  a blood-alcohol  content  of 0.04  or

above  to  be  intoxicated.  The  state  of  Pennsylvania  considers  drivers  with  a  0.10

reading  to  be  intoxicated  and  unfit  to  drive. The NRC  is  considering  whether to  issue the  company  a  violation for the incident  or  revoke the  operator's  license. (See  November  14,  2003,  for  a  related d e v e l o pme n t . )

May 21, 2003  --EXELON'S FORMER CHIEF EXECUTIVE MADE THE TOP

10 LIST OF BEST-PAID U.S.  energy  executives for  2002,  according to  a

compilation  by  the  Platts  Energy  Business  &  Technology  (EB&T)  magazine.

Corbin McNeill,  Jr., the  ex-chairman  and  co-CEO  of Exelon Corp.  had  a

compensation  package  of  nearly  $29.8-  million  last  year,  making  him  the  fourth

highest  paid  CEO  out  of the  250  executives that  were  examined. McNeill's  2002

package  included  a  severance  payment  and  benefits  from  a  pension  benefit  plan

from  PECO  Energy.  He  retired  from  Exelon  in April  2002.  The  highest-paid

executive  in  2002,  at  $46.6-million,  was  Charles  Watson,  former  CEO  of  Dynegy

Inc., the  EB&T  listing  shows.  The  survey,  which  will  be  published  in the  June

issue  of EB&T,  considered the  executives'  salary,  bonuses,  restricted  stock

awards,  underlying  options,  value  of  options  exercised,  long-term  investment

pool  pay  outs,  and  any  other  compensation. (See  July  9,  2003, for  staff  cuts).

May  22,  2003 - The   NRC identified  a Green  violation  relating to

Appendix R, i.e., fire protection. The NRC deemed the issue  as being  of  “very low

safety  significance”  (IR  50-277-03-009; IR-50-278/03-009).

This was the thirty-fourth Non-Cited  Violation since June 1998.

Exelon's total  cost  avoidance, i.e., “credit” for 34 Non-Cited Violations =

$1 ,720,000.

- May 22, 2003  -- THE PENNSYLVANIA NATIONAL GUARD IS

INCREASING ITS PRESENCE  at the  state's nuclear plants, Gov. Edward Rendell

(D)  announced  yesterday.  Since  shortly  after  the  Sept.  11,  2001  terrorist  attacks

until  the  end  of  last  month,  Pennsylvania  had  had  a  24-hour  Guard  presence  at

the  plants,  but  then  had  switched  to  random,  unannounced  security  patrols,

Rendell  spokesman Michael  Lukens  said. But  under  Rendell's  order,  which  went

into  effect  yesterday,  the  two  elements  are  being  combined,  Lukens  said.

...Continued on the following page...He  said the  order would  remain  in  effect  "indefinitely,"  and the  governor's  office would  continue to  assess it. Rendell's  announcement  said he took the  action in response to the  recent  elevation  of the  national threat  level to  orange,  but  Lukens said the  state's  assessment  of the need for the Guard would not necessarily be tied to  future  changes  in  that  threat  level.

( Platts Nuclear News Flashes. ( See October 6 &  17, 2001, January 30,

2002,   and  November  2,  2002   for   related  incidents).

May  28,  2003 -A  License Event  Report  was  generated  after  “licensed

operators  were  notified  that  approximately  4  inches  of  water  [170  gallons]  was

discovered  at the  bottom  of the  ‘A’  Standby  Gas  Treatment (SBGT)  filter  plenum

during  the  performance  of  annual  surveillance   (IR  50-277/2003004; IR-50-

2 7 8 / 2 0 0 3 0 0 4 ) .

- June 13, 2003 - LOSS OF BOTH OFFSITE POWER SOURCES TO

TECHNICAL  SUPPORT CENTER:   "During  severe thunderstorms  in the  area

power  was  lost to the  onsite technical  Support  Center (TSC)  for  approximately  90

minutes.   These storms   caused both offsite power sources to the TSC to deenergize  at  2021.   Grid  operators  began  restoration  activities  immediately  and

power  was  restored  to  the  facility  at  approximately  2200. Investigation  is  in

progress for the cause of the line tripping."

The licensee notified the NRC Resident Inspector.

June 17, 2003 - Pensions: Utility Obligations Add Up,

By Ken Silverstein Director, Energy Industry Analysis Utilities may get socked again.

Already,  stock  values  and  credit  ratings  have  taken  a  hit  because  of  the

failure  to  mitigate  risks  to  their  unregulated  operations.  Now,  their  credit  status

may  get  cut  even more,  given  the  level  of  "unfunded"  pension  liabilities.

If the money  in the  pension  plan to  pay  retirement  obligations falls  short, then  a

"minimum  pension  liability"  must  be  recorded  on  the  financial  statements. In

lay terms,  it means that  if  a  company  were to  be  liquidated today, then  it  would

be  compelled to  pay  up. The  liability  recorded  could therefore  impede the  debt-tocapital  ratio,  which  could  harm  credit  quality  and  even  trigger  violations  of

covenants. And  while  regulated  utilities  have  a  chance  to  recover  such  costs  from

their  customers,  many  are  now  in  the  midst  of  rate  moratoriums  and  cannot

seek  recovery,  says  Steven  Fleishman,  analyst  with  Merrill  Lynch  in  New  York

City.  Others  would  prefer  to  avoid  a  rate  case,  given  that  regulators  may  revisit

their  entire  rate  structure  and  reduce  their  allowable  returns,  he  adds.

...Continued on the following page...Those  with  the  largest  underfunded  pensions  at  year-end  2002,  says  Merrill Lynch,  include  Exelon  ($2.4  billion),  FirstEnergy  Corp.  ($977  million),  Public Service  Enterprise  Group  ($837  million)  and  American  Electric  Power  ($788 million.)  Companies  with  the  largest  underfunded  pensions  as  a  percentage  of equity  market  value,  include  CMS  Energy  (60  percent),  Sierra  Pacific  Resources (30  percent),  AES  Corp.  (29  percent)  and  CenterPoint  Energy  (17  percent). FirstEnergy, for  instance,  has  said that  its  pension  liabilities  had forced  it to  cut its  2003  earnings  picture.  Profits,  it  says,  will  grow  by  4-5  percent-not  the  7-8 percent  that  it  had  projected.  DTE  Energy,  meanwhile,  said  that  its  pension expenses  would  be  $50-$55 million  higher  in  2003 than  in  2002. (See  December 3,  2003,  for  related  GAO  Study).

- July 9, 2003 --EXELON HAS RESTRUCTURED ITS NUCLEAR

OPERATIONS BY ELIMINATING  regional operating  groups in favor of  a  single

organizational  unit.  The  restructuring  was  made  public  today  in  an  NRC  Weekly

Information  Notice,  but  was  announced  internally  to  Exelon  employees  June  23.

As  part  of the  restructuring,  Chris  Crane  was  named  chief  operating  officer  of

Exelon  Nuclear, William  Levis  vice  president  of  mid-Atlantic  operations,  and

Chip  Pardee  senior  vice  president  of  nuclear  services. Also,  Robert Braun  will

replace  the  retiring  Joel  Dimmette  as  vice  president  of  nuclear  operations.  The

changes  will  become  effective  by  Aug.  1,  said  Exelon  spokeswoman  Ann Mary

Carley.  She  said that  when  Exelon  Nuclear  was  formed  in  2002,  it  set  up the

regional  operating  groups  to  accommodate  the  nuclear  organizations  of  the

former  PECO  Energy  and  Commonwealth  Edison (ComEd),  as  well  as  AmerGen,

a  joint  venture  between  Exelon  and  British  Energy.  Exelon  was  created  by  the

merger  of  PECO  and ComEd  parent  Unicom Corp.  Over time, the two  regional

groups'  policies  and  procedures  have  aligned  and  all  10 Exelon  plants  are  now

using the  same  policies  and  procedures, Carley  said (Also  refer to   May  21,  2003

--EXELON'S FORMER CHIEF EXECUTIVE MADE THE TOP 10 LIST OF BEST-PAID

U.S.  energy  executives  for  2002,  according  to  a  compilation  by  the  Platts  Energy

Business  &  Technology  (EB&T)  magazine.  )

July  11,  2003 - The NRC  conducted  a  supplemental  inspection to  “assess

the  licensee's  evaluation  and  corrective  actions  regarding  the...June  2,  2002,

carbon  discharger  event”.  The  NRC  diluted  its  previous  “White”  finding  and

noted  the  event  “will  only  be  considered  in  assessing  plant  performance  through

the  period  concluding  at the  end  of the  second  calendar  quarter  of  2003...” [In

other  words,  20  days  from the  NRC’s  promulgation the  event  becomes  a  “nonevent”.]    (See  November  26,  2002  additional  data.) (IR  Supplemental  Report

5 0 - 2 7 7 - 0 3 - 1 1 ;   5 0 - 2 7 8 / 0 3 - 0 1 1 ) .

This was the thirty-fifth Non-Cited  Violation since June  1998. Exelon's

total  cost  avoidance, i.e., “credi t” for 35 Non-Cited Violations = $1 ,775,000.

July  16,  2003 - The NRC’s Office  of Investigation’s (OI)  concluded that

Exelon  was  in  violation  of  a  License Amend met  Restriction that  requires

notification  when  a  reactor  operator  (RO)  medical  status  changes.  Such  a  change

occurred  to  an  RO  on  September  13,  2001,  and  the  forenamed  operator  returned

to  work  between  April  and  December  2002  without  notifying  the  NRC  about  the

reactor  operator  Fitness for  Duty  in the  control  room.

The  NRC’s  investigation  began  on  January  3,  2003.  “After  careful

consideration  of  the  information  developed  during  the  investigation,  the  NRC

has  concluded that  a  violation  of NRC  requirements  occurred” (PBAPS, NRC  O&I

No.  1-2003-002).

This was the thirty-sixth Non-Cited  Violation since June  1998. Exelon's

total  cost  avoidance, i.e., “credit” for 36 Non-Cited Violations = $1 ,830,000.

July  22-29,  2003  -  Unit  2  experienced  an  automatic  reactor  shutdown

“due to  generator  lockout  from  foreign material  causing  a  short  in the  bus  duct.

Unit  2  returned  to  100%  power  on  July  29,  2003.”   (IR  50-277/2003004; IR-50-

2 7 8 / 2 0 0 3 0 0 4 ) .

On  July  22,  2003,  “Unit  2  shut  down  when  a  piece  of  broken fan  belt

entered the  reactor’s  isophase  bus  duct  cooling  system. Exelon found that  a

design  weakness  existed  and  decided to  install  debris  guards that  would  prevent

beltmaterial  from  entering  the  fan  suction.”

“Despite  Exelon’s  intention  to  install  fan  belt  guards  within  30  days,  the

corrective  action  took  two  months  “with  no  rationale  provided  for  the  delay,”

according  to  the  inspection  report”  (“York  Sunday  News”,  March  13,  2005).

July 23, 2003 -   PEACH BOTTOM-2 REMAINED DOWN TODAY AFTER

TRIPPING AUTOMATICALLY  yesterday  due to  an  actuation  of the main

generator  protective  relay,  Exelon  spokeswoman  Dana  Fallano  said.  She  said

Exelon  is  investigating the  root  cause  of the  actuation (Source: Platts, Nuclear

News) .

July  24,  2003 - The   NRC  identified  a  Green  violation  relating to the

inoperability  of   ‘A’  train   was  inoperable  between  November  200s  through  may

28,  2003  (IR  50-2772003003  IR-50-278/2003003). This was the thirty-seventh   Non-Cited  Violation since June 1998. Exelon's total  cost  avoidance, i.e., “credit” for 37 Non-Cited Violations = $1,885,000.

July 29, 2003 - 11:55:05 AM EST   Peach  Bottom plant back to full power; Shutdown of nuclear generating   unit 2 last week cited as non emergency By LANCASTER INTELLIGENCER  JOURNAL

The  Peach  Bottom Atomic  Power  Station  returned to  full  power today  after

an outage of one of its two power  generation  reactors last week.

Peach  Bottom's  Unit  2  reactor  returned  to  service  at  about  10:15  a.m.

Saturday.  As  of  yesterday,  the  unit  was  operating  at  approximately  90  percent

of  capacity,  said  Dana  Fallano,  spokeswoman  for  Exelon  Nuclear,  which  owns  the

plant. Unit  2  shut  down  one week  ago  after  generator  problems forced  an

automatic  shutdown.

Neil  Sheehan,  spokesman  for  the  Nuclear  Regulatory  Commission,  said  all

safety  systems  functioned  properly  during  the  shutdown  and  any  radioactive

steam that  could  have  been  released  was  contained  and  isolated  in the  reactor

vessel.   "It  seems  like  a  pretty  straightforward  event,"  he  said.

Exelon  reported the  shutdown to the  NRC  at  5:30  p.m.  July  22.  The

commission  classified the  shutdown  as  a  "non  emergency  event."

According  to  Exelon's  event  report,  Unit  2's  generator  malfunctioned  at

1:45  p.m.  that  afternoon  while  operating  at  full  power. With  no  way  to  output

electricity,  the  plant's  main  turbine  tripped  off,  which  then  triggered  an

automatic  reactor shutdown. Exelon  employees  had  no firm  answers  last  week  on  what  caused the generator  to  malfunction,  Sheehan  said. Yesterday,  Fallano  said  the  generator's  protective  electronic  relay  system activated  after  sensing  some  type  of movement.  She  said  the  company  is  still investigating  what  type  of  movement  that  was. NRC  reaction: Sheehan  said it's unlikely the NRC will  send a team of inspectors

to  investigate  because  the  problem  occurred  in  the  generator,  not  the  reactor

vessel,  and  the  shutdown  appears  to  have  gone  smoothly.

The  utility  may  be  concerned,  Sheehan  said,  about  losing  a  reactor  during

heavy  summer  demand  for  electricity.  Fallano declined  to  discuss  how  much

revenue  was  lost,  calling  it  private,  competitive  information.  When both  Peach

Bottom  reactors  are  running,  the  power  station  supplies  enough  electricity  for  2

million  homes.

...Continued on the following page...The event marked the second shutdown  at  Peach Bottom's  Unit  2  in  seven months.  On average, the nation's 103 commercial  reactors  automatically  shut

down  only  once  every  other  year,  according  to  the  NRC.

On  Dec.  21,  computer  failure  closed  valves  that  direct  steam  from  Peach

Bottom's  Unit  2  to  the  main  turbine  that  generates  electricity.  The  reactor

automatically  shut  down  to  avoid  a  steam  buildup.

The NRC  sent a team of inspectors to the plant and  cited Exelon for two

safety  violations  involving  human  errors  and  equipment  problems  that  occurred

during  that  shutdown.

Staff writer Charlie Young contributed to this report.

July 30, 2003   - EXELON REPORTED SECOND QUARTER 2003

EARNINGS  OF  $402-MILLION,  an  8.9%  increase  over the  $369-million  earned

in the  same  quarter  one  year  ago.  The  company  said  an  increase  in  sales,  lower

interest  expense,  and  lower  depreciation  and  amortization  offset  weather-related

decreases  in  electricity  deliveries  and  lower  energy  margins  at  Energy  Delivery.

Exelon  reported  its  nuclear  fleet,  excluding  the  plants  in  the  AmerGen  joint

venture  (Clinton,  Oyster  Creek  and  Three  Mile  Island-1)  generated  29,619

gigawatt-hours  in  the  second  quarter,  compared  to  28,776  GWH  in  the  second

quarter  of  2002.  Capacity  factor  of  the  Exelon  fleet,  including  the  AmerGen

plants,  improved  to  94%  during  the  second  quarter  this  year  from  92.1%  in

the  second  quarter  last  year,  Exelon  reported.  AmerGen  is  a  joint  venture

between  Exelon  and  British  Energy (Source: Platts,   Nuclear  News) .

August  8,  2003 - The   NRC  identified  a  Green  violation  “concerning the

failure  to  properly  correct  an  equipment  deficiency  that  subsequently  resulted

in  a  challenge to the  plant  and  operators.  Specifically,  a  solenoid  associated  with

a  reactor  feed  pump  turbine (RFPT)  overspeed  trip  device  exhibited  degradation

during  RFPT  overspeed testing  on two  occasions [September  27  and  November

27,  2001],  however,  your  staff  failed  to  determine  the  root  cause  for  this

problem  until  a third  problem  occurred that  resulted  in  a  RFPT trip  and  plant

transient”  (IR  50-2772003012  IR-50-278/2003012).

This was the thirty-eighth Non-Cited  Violation since June  1998. Exelon's

total  cost  avoidance, i.e., “credit” for 38 Non-Cited Violations = $1 ,940,000.

August  14,  2003 -  “...the  fifth  stage  feed  water  heaters  were  removed

from  service  for  end  of  cycle  coast  down.” (IR  50-277-200-3004; IR-50-278/200-

3 0 0 4 ) .          Exelon Corp debt ratings unchanged by Sithe deal-S&P

(NEW YORK, Aug.  18 -  Standard  & Poor's  Ratings  Services  said today that

its  ratings on Exelon Corp. (nyse: EXC - news - people) (A-/Stable/A-2)  and its

subsidiaries  will  not  be  affected  by  the  company's  announcement  that  it  will  sell

50%  of  its  equity  interest  in  Sithe Energies Inc.  Further,  subsequent full  sale  of

Sithe,  which  remains  a  distinct  possibility  given  the  put  and  call  options

attached  to  Sithe  ownership,  would  not  affect  Exelon's  ratings...Exelon's

announced  equity  interest  sale  demonstrates  the  company's  intention  to  sell  off

the  disappointing  merchant  assets  it  acquired  several  years  ago,  a  positive  for

credit  quality.  However,  the  fact  that  Exelon  recorded  a  $200  million  writedown  related  to  its  original  49.9%  investment  in  Sithe  demonstrates  the

inherent  risk  associated  with  the  remaining  high-risk  portion  of  this  business.

Copyright  2003,  Reuters  News  Service.

(See  August  29,  2003  for  a  related  development).

August  24,  2003 -  “The  fourth  stage  feed  water  heaters  were  removed

from  service [for  end  of  cycle  coast  down]”. (IR  50-277-200-3004; IR-50-

2 7 8 / 2 0 0 - 3 0 0 4 )

POLL: Security officers expect another blackout in 12 months

August  25,  2003 - CSO Magazine  polled  382  chief  security  officers (CSO)

and  senior  security  executives  showed  59%  blamed  the  electric  industry  and  not

the  government  for  the  blackout  of  2003.

CSOs  showed their lack of  confidence in the power industry and grid with 59%

predicting  another  major  blackout  within  12  months.  Over  three-quarters  said

they  doubt  the  electric  industry  will  be  modernized  in  five  years.  That

percentage  want  a  probe  by  an  independent  investigator  without  ties  to  the

industry.   Almost  half (47%)  ask that the  probe's  results  be  classified to  keep

terrorists  from  learning  about  US  vulnerabilities.

Those  surveyed included  156 whose firms felt  some direct impact of the

outage.  Many  want  the  federal  government  to  expand  oversight  of  the  electric

industry.  "Regulations  are  often  regarded  as  the  necessary  evil  in  securing  the

nation's  infrastructure,"  said  Lew  McCreary,  editor  of  the  Framingham,  Mass,

publication,  but  he  was  surprised  that  CSOs --  traditionally  anti-regulation --  are

calling  for  increased  government  control  in  this  industry,  "having  now  been

faced  with  a  glaring  example  of  so-called market forces  at  work," the  editor

cleverly  observed.

...Continued on the following page...

The magazine did the  survey  online Aug  19-21, having  sent  an  email invitation  to  the  web-based  survey  to  12,200  subscribers.   The  382  are  the  ones

that  met  qualifications  and  fully  completed  the  survey.   The  sample  was  chosen

randomly  and  each  subscriber  had  an  equal  probability  of  being  selected.   Figure

a  5%  margin  of  error,  the  magazine  said.

Results  are  at www.csoonline.com/releases/  08220385_release.html.

(Story  originally  published  in  Restructuring  Today 8/25/03)

Raytheon Also Sues BNP Paribas Over Exelon Projects

August  29, 2003 - LEXINGTON, Mass. -(Dow  Jones)- Raytheon Co.

(NYSE:RTN - News)  sued  an indirect  subsidiary of Exelon Corp. (NYSE:EXC -

News) , as well as BNP Paribas SA , about Exelon's decision to turn over the

subsidiary  to  its  bank  lenders.

Raytheon  said it is  "seeking to  protect  Raytheon's  rights" in  connection

with the Exelon Mystic  and Exelon  Fore  River  power  plant  projects  in

Massachusetts. In  a  press  release, the  aerospace  and  defense  company  said the

suit  was  filed  in Massachusetts'  Suffolk  County  Superior  Court.

On  July  29, Exelon  said  it  planned to turn Exelon Boston  Generating  LLC,

its indirect  subsidiary, over to its bank lenders. It decided to do  so  after  continued

evaluation  of  Boston  Generating's  power-plant  projects  and  discussions  with

l ende r s . Raytheon turned  over the Mystic  and Fore  River  projects to  owner Exelon -

one  in April,  one  in  July. The  projects  weighed  down  Raytheon's  balance  sheet for

several  years.

Raytheon  was forced  back  into the  construction  business to  complete the

projects  in  Weymouth  and  Everett,  Mass.,  after  Washington  Group  International

Inc.  (NasdaqNM:WGI I - News) filed for  bankruptcy. Representatives  from  Exelon  and  BNP  Paribas  were  not  immediately available  to  respond  to  the  lawsuit.

Raytheon  named the Mystic  and  Fore  River  units  as  defendants  as  well.

...Continued on the following page...Raytheon  said  that  since  Exelon's  announcement,  Raytheon  has  continued to perform final  close-out work on the projects. Raytheon  said it  seeks to  "obtain adequate  assurances  of  payment"  and  protect  its  rights  under  its  support agreements. Raytheon,  through  a  subsidiary,  was  the  original  contractor  of  the  plants.

It  sold that  subsidiary to Washington  Group  in  2000,  but  got  project

responsibility  back  in  a  settlement  from  Washington  Group  after  Washington

filed  for  bankruptcy  in  2002.Exelon  seeks to transfer  ownership  of Boston  Generating  without the subsidiary  filing  for  bankruptcy.  Exelon  has  about  $700  million  invested  in Boston Generating.   Exelon has  said it plans to  spend nothing further on Boston Generating  outside  of  limited  administrative  and  operational  services.Therefore,  Raytheon  is  seeking  a  declaratory  judgment  and  injunction

from the  court that  will  assure  it  is  paid  by  either Exelon,  its  subsidiaries  and

subunits,  or  its  lenders.Exelon  has  refused to  refund  about  $36 million  in  prepaid  liquidated damages  that  Raytheon  advanced,  the  court  papers  said.  Raytheon  also  said  that the  defendants  have  no  right to  draw  upon  about  $73 million  in  letters  of  credit that the  defense  contractor posted for them.  Raytheon  said it  posted the  credit to ensure  the  performance  of  its  contractual  obligations. Throughout  the  court  filing,  Raytheon  says  that  it  spent,  during  the lifetimes  of  its  guarantee  agreements, more than  $1  billion for the  benefit  of Exelon,  its  subsidiaries  and  subunits,  and the  lenders. BNP  Paribas'  alleged  role  in  the  matter  dates  back  to  January  2001,  when

a  former  owner  of  the  plants,  Sithe  Generating,  secured  financing  from  the

French  bank to  pay for the  construction  of the Mystic  and  Fore  River facilities.

After Washington  Group  abandoned  work  on the facilities, BNP  and  other  lenders

insisted  on  credit facility  changes.  One  of those  changes  was that BNP,  court

papers  indicated,  would  provide  Raytheon  with  prompt  written  notice  of  any

continuing  events  of  defaults  under  the  credit  agreement. Raytheon  said that,  from  November  2002 --  when  Exelon  bought  Sithe -- to the  day Exelon  announced  it  was  handing the  units  over to  its  lenders,  it never  received  any  notices  from  BNP  Paribas. Because  of the lack  of notice, Raytheon  claims it has  continued to  spend

money  in  good faith  and  has  been  damaged  by BNP's  alleged  omissions.

-Thomas  Derpinghaus;  Dow  Jones  Newswires;  201-938-5400.

(See  August  29,  2003  for  a  related  development).       The commission investigated a loss of power at

Peach Bottom’s  power station in May

By SEAN ADKINS Daily Record

September  4,  2003 -   For  about nine days in May,  an undetected  broken

wire  caused a   loss of power to a  redundant  control  station for Peach Bottom

Atomic  Power  Station  Unit  3.

A failure to observe work order test instructions after   maintenance on the

panel  prevented  plant  technicians  from   immediately  discovering  the  broken

wire,  according  to  a  U.S.   Nuclear  Regulatory  Commission  report.

Damage to the power  supply wire occurred during   maintenance to the highpressure  coolant  injection  alternative   control  station —  a  system  used to  shut

down the plant if the   operators  are forced to leave the main  control  room

because of  a   fire,  said NRC  spokeswoman Diane Screnci.

While the violation is under commission  review, the incident did not pose a

safety threat  since the  plant  repaired   the  wire  and  restored  power to the  back-up

station  on May  14,   Screnci  said.

“There are other ways  you  could  shut down the plant  even if  you don’t have

the  station  active,”  she  said.

Depending on the  commission’s findings, the infraction could mean

additional  plant  inspections.

- In June, Peach Bottom Atomic Power Station was the subject of a

supplemental  NRC  inspection  for  a  violation   committed  the  year  before.

Last year, a light bulb dropped from the ceiling onto a circuit board and

caused the  plant’s fire-suppression  system to  discharge  carbon  dioxide [Refer to

July  11,  2003]  into  the  E-3  emergency  diesel  generator  room  in  the  Diesel

Generator  Building.

The  supplemental inspection found that the plant had taken the proper

corrective  actions  and the  power  station  could  return to  a  routine  inspection

s chedul e .

While the plant  showed that its fire-suppression  system was in working

order,  a malfunction  in  one  of  its  diesel  generators  garnered  a  non-cited

commission  violation  of  very  low  safety  significance.

Continued on the following page...         In June, NRC inspectors found that Exelon technicians had not adequately

tightened the  engine top  cover flange  joint  bolts  of  an  emergency  diesel

generator  during  a  maintenance  procedure.

As a result, lube oil leaked from the joint and caused a small fire on the

exhaust  manifold  during  a  test.

During that  same time period, Three Mile Island Unit  1 violated an NRC

reporting  requirement.

In June, NRC inspectors found that, on three instances, TMI officials found

potentially  disqualifying  medical  conditions  among  its  licensed  operators  but

had  not  reported them to the  NRC  within the  required  30  days.

TMI  requested its doctor to  confirm with the patient’s physicians, which

extended  past  the  30-day  NRC  reporting  period.

Two units at nuke plant shut down; grid disturbance cited

September  15,  2003    - An  electrical disturbance  on the power  grid  cut  off

incoming   electricity  at  the  Peach  Bottom  nuclear  power  plant  and  caused

both  reactors  to  shut  down  automatically  early  Monday,  Exelon   Nuclear

officials said.

Plant  officials  declared  an  "unusual  event"  just  after  2:30  a.m.

The  plant's  four  emergency  backup  diesel  generators  provided  emergency

power for  about  an hour,  said Exelon  spokesman David Simon. One of the

generators malfunctioned,  and then  another   backup  source  of  power  was  used to

power  vital  equipment,  such  as  lights  and  emergency  feed  water  pumps,  until

power  was  restored  later  in the morning,  Simon  said.

...  PJM Interconnection, the  company that  operates the  power  grid  in the

Mid-Atlantic,  said  it  was  investigating  the  grid  disturbance.   PJM  spokesman

Ray  Dodter  said the  company  couldn't  yet  say  what   caused  the  disruption.

©NEPA News 2003

- Unit-2 was operating at 100% power, and retuned to full power on

September  25,  2003.

- Unit-3 was operating at 91% power, and remained shut for the

3R14  refueling  outage.

- September  15, 2003 --THE U.S. COAST GUARD PROPOSED

ESTABLISHING A PERMANENT SECURITY ZONE on the waters adjacent to

Peach Bottom. According to  a notice  of  proposed  rulemaking  published  in

yesterday's  Federal  Register, the  zone  "would  protect the  safety  and  security  of

the  plant  from  subversive  activity,  sabotage,  or  terrorist  attacks  initiated  from

surrounding  waters.  This  action  would  close  water  areas  around  the  plant."  A

temporary  final  rule  issued  June  4  established  the  security  zone  on the

Susquehanna  River  by  restricting  any  person  or  vessel  from  entering  or

navigating  the  security  zone  without  Coast  Guard  permission.  The  Coast  Guard

said  in  the  notice  that  it  wants  to make  the  security  zone  permanent.  Comments

on the proposed  rule are due by Nov.  14. (Source: Platts,   Nuclear  News) .

October 24, 2003 - Exelon Corp. Posts Quarterly Net Loss of $102 Million

-  Oct.  24--Commonwealth Edison  parent Exelon Corp.  reported  solid  operating

profit  in  the  third  quarter,  but  special  items --  including  a  mammoth  $573

million  charge  to  write  off  a  disastrous  investment  in  East  Coast  electricitygenerating  projects --  pushed the  holding  company's  bottom-line  results  into the

red. In the latest  quarter, Exelon  reported  a net loss  of $102 million,  or  31  cents  a

share. (Knight Ridder Tribune Business News.)

October 27, 2003 -NRC AGREED TO RELAX TWO REQUIREMENTS IN

AN APRIL ORDER ON SECURITY FORCE personnel working hours. NRC Office of

Nuclear  Reactor  Regulation  Director  James  Dyer  Oct.  23  issued  notices to  all

reactor  licensees  that  the  agency  would  allow  shift  turnover  time  to  be  excluded

from total  group  work  hours that must  be tracked.  The  NRC  staff  had  wanted

accounting  of  all  hours  worked  for tracking  overtime,  which  it  says  could  lead to

worker  fatigue,  but  now  agrees  with  the  industry  that  tracking  the  extra  time

does  impose  some  additional  burden. Industry  officials  argued the  shift  change

time  is  usually  not  more  than  15  minutes.  The  second  relaxation  allows  licensees

to increase the work hours during force-on-force  exercises from  a 48- to 60-

hour  per  week  average.  Dyer  said  the  staff  understands  that  the  simulated

exercises  put  additional  demands  on  the  security  guards  but  the  mock  attacks

extend only for a short period of time (Platts,   Nuclear  News) .

October 29, 2003 --OPERATING POWER REACTOR LICENSEES MUST BE

IN FULL COMPLIANCE TODAY with NRC's April 29 order imposing measures to

control the  work  hours for  security force  personnel.  The  industry  had  asked for

relief in two  areas  of the  order,  and the NRC  staff  recently  approved those

requests.  The  industry  will  not  have to track the time  it takes  for  guards to

change  shifts  in the  overall  group  work  hours  and  will  be  allowed  a  60-hour

limit--up  from  the  usual  48  hours  per  week--in  scheduling  guards  during  the

week of a force-on- force  exercise. Two other April orders, one on  security officer

training  and the  other  on  changes to the  design  basis threat,  require  full

implementation  by  Oct.  29,  2004.  A  Nuclear  Energy  Institute  official  said  at  a

conference  in  Arlington,  Va. today that the  industry  plans to  ask the  NRC to

rescind  the  three  orders  after  licensees  adopt  the  requirements  in  their  security

plans (Platts,   Nuclear  News) .

November  3, 2003 - S&P placed Exelon  on  credit watch   after the

Company  announced  it  wanted  to  buy  Illinois  Power  from  Dynergy.

or  $2.2  billion,  if Illinois  legislators  grant  it  single-digit  rate  increases.

The  deal  was canceled after Exelon determined it  could not  count on  rate

increases.

November  4,  2003 - NRC  inspectors  identified three,  "Green”  non-cited

violations  and  Severity  Level IV  violation  “associated  with  a  lack  of  records to

support  changes  made  to  the  emergency  plan”  (IR  50-277-200-3004; IR-50-

278/200-3004).

The  Severity  Level IV  Violation,  also  Non-Cited,  involved  changes  to

Exelon’s  Standard  Emergency  Plan,  including  Limerick,  Peach  Bottom  and

Three  Mile  island.  Exelon  changed  “emergency  plan  commitments  without

documentation”  which  subsequently  impacted  “the  NRC’s  ability  to  perform  its

regulatory  function...”

Continued on the following page...The  three  other  “Non-Cited”  violations  include  different  aspect  of  plant

operations  and  training:

Licensed  Operator  Requalification  “Green.  A  non-cited  violation...was

identified  regarding  the  licensee’s  method  used  to  reactivate  senior  operator

licensees  to  support  refueling.  The  operators  were  reactivated  without  the

required  direct  supervision  being  present  during  the  shift  under-instruction

item.  The  Limited  Senior  Reactor  Operator (LSRO)  Requalification  Program  for

Fuel Handlers is  a dual  site  operator license  program that  applies to  both

Limerick  and  Peach  Bottom  sites.”

Finding  1 -Unit  2  Reactor Core Isolation Coolant  System  During Unit  2

S c r am “...Exelon  did  not  adequately  correct  a  significant  condition  adverse  to

quality  identified  during  a  December  21,  02  scram,  associated  with  the

inoperability  of the Unit  2  reactor  core isolation  cooling (RCIC)  pump in the

automatic  flow  control  mode”

Finding  2  -Unit  2   Main  Steam  Line  High  Temperature  Switch “..during

the  period  of  July  2001  through  July  2003,  Exelon  did  not  adequately  correct  a

condition  adverse  to  quality,  specifically  a  high  Unit  2  steam  tunnel

temperature  condition  that  was  not  representative  of  a  steam  leak”.

This was the thirty-ninth, fortieth, forty-first and forty-second  Non-Cited

Violat ion since  June  1998. Exelon's total  cost  avoidance, i.e., “credi t” for 42

Non-Cited Violations = $2, 160,000.

November  7, 2003 -   “NRC: NRC Appoints New Senior Resident Inspector

at the  Peach Bottom...Craig   Smith  is the  new  senior  resident  inspector  at the

Peach Bottom   Atomic Power Station in Delta, Pa. The two-unit  site is  operated

by Exelon.   Most  recently, Mr.  Smith  was  a  resident  inspector  at the  Three

Mile Island  nuclear  plant  in Middletown,  Pa.”   (“NRC Press  Release”).

However,  Eric  Epstein,  Chairman  of  TMI-Alert,  noted: “Craig  Smith  was  at

TMI for five  years  and  hid  on the Island  except for  annual  appearances.” Mr.

Epstein  pointed to Mr.  Smith’s last  appearance  before the public  at the NRC’s

Annual  ROP  Assessment  meeting  on  Wednesday,  April,  9,  2003.

Continued on the following page...Mr.  Smith  stated   that the  number  of  employees  at TMI  was  529. When the

NRC   was  apprised  that  they  were  off  by  114  employees,  they  reassured  the

community  it  didn’t matter  how many  people  worked  at TMI   based  on the  color

code, PI  sequence and late hour. Local  residents   persisted, and told the NRC that

Performance Indicators for Non- Performance does make  sense,   and we’re  still old

fashioned enough to   prefer Zero Tolerance to  color-coded lollipops.

- November 8, 2003 - U.S. Warns of Al Qaeda Cargo Plane Plot -

WASHINGTON (AP) --  The  latest  warning  from  the  Homeland  Security

Department  that  al-Qaida  may  be  plotting  an  attack  is  renewing  calls  for  stricter

security  on  cargo  planes.

The  department  advised  law-enforcement  officials  Friday  night  of  threats

that  terrorists  may  fly  cargo  planes  from  another  country  into  such  crucial  U.S.

targets  as  nuclear  plants,  bridges  or  dams,  Homeland  Security  spokesman  Brian

Roehrkasse (By THE ASSOCIATED PRESS/Published:  Filed  at  4:29  p.m. ET).

November  13,  2003 -  “Exelon  Nuclear’s  Peach Bottom-2  was forced to

shut  down  196.3  hours  due  to  off-site  voltage  fluctuations  in  the  elcxtrical  grid”

(Nucleoniocs  Week, p. 17.)yees  screened  positive for the  illegal  drug  ˜ the  largest  single  six-month  j

- On drugs, and on the job, Between July 1999 and December 2002, 143

workers at local power plants tested positive for drugs or alcohol.

By  SEAN  ADKINS  ,  Daily  Record  staff (November  14,  2003)

Late  in the  afternoon  of  Sept.  24,  1999,  a  Three Mile Island  security  officer

checked  a  tip  about  a  short-term  contractor  smoking  marijuana  on  the  job.

Officer  Darlene  Ranck  escorted  George  Lonnie McDaniel,  27, to TMI's  security

office to  be  questioned  for  violating the  plant's  Fitness-for-Duty  Program.

Ranck  and Officer Greg DeHoff  asked McDaniel to  empty his pockets.

The  Jessup,  Ga.,  resident  pulled  a  small  plastic  bag  of marijuana from  his

pocket,  and  plant  security  officers  called  the  Pennsylvania  State  Police,

according  to  an  affidavit  filed  with  District  Justice  David  H.  Judy  in  Dauphin

C o u n t y .

McDaniel's job  at TMI did not  grant him  access to  vital  areas of the plant.

Currently,  Dauphin  County  has  a  fugitive  warrant  out  for  McDaniel's  arrest.  He

could  not  be  reached for  comment for this  article.

Between  July  1999  and  December  2002,  143  workers  and  short-term

contractors  at Three Mile Island  and  Peach Bottom Atomic  Power  Station tested

positive  for  drugs  or  alcohol,  according  to  biannual  Fitness-for-Duty  reports.

- The  York  Daily  Record  obtained the  reports from the  U.S.  Nuclear

Regulatory  Commission  through  a  Freedom  of  Information  Act  request.

Drugs  listed  in  the  reports  include  marijuana,  cocaine,  opiates,

amphetamines  and  alcohol. All the  workers tested  were  people  who  had  or  were

applying  for  unescorted  access  to  vital  areas  of  the  plants.

Many  were  short-term  workers,  such  as  McDaniel.  They  travel  the  nation,  from

power  plant to  power  plant, to  work  when  reactors  are  shut  down  for  refueling.

Continued on the following page...State  Rep.  Bruce  Smith,  R-Dillsburg,  said  he  was  disturbed  by the  number of positive drug tests  reported by TMI officials.  “There is no  excuse or  any way to defend  substance  abuse  at  a  nuclear  power  plant,”  he  said.

Smith  said he  plans to  contact the NRC  and  acquire the  plant's Fitness-forDuty  reports  for  his  own  records.  A  Daily  Record  investigation  found: XB7; More people might have tested positive, but the NRC does not have a  zerotolerance  policy  when  it  comes to  chemical testing.  The  commission  uses  cutoff  limits to  screen for narcotics  and  alcohol. For  example, the NRC’s limit for  alcohol is  a  blood-alcohol  content  of  0.04  percent.  That  is  equivalent to three  12-ounce beers  in  an  hour for  a  200-pound man. XB7 ; Short-term  contractors made  up the majority  of the  workers  who tested

positive  at  both Peach Bottom  and TMI  unit  1  in Londonderry Township,

Dauphin  County.  Short-term  contractors  generally  handle  maintenance  and

repairs  that  cannot  be  completed  when  the  plant  is  on-line. XB7 ; Workers  inability to  cope  with  stress  following the terrorist  attacks may have  contributed  to  the  largest  single  six-month  jump  in  marijuana  use  among plant  workers  since  July  1999.  For  both  plants,  73  people tested  positive  for  marijuana  ˜  the  most  of  any  intoxicant. Keeping fit for duty In  1989, the  NRC  created  a  policy that  each  plant  should follow  an individual  fitness-for-duty  program.  Collecting  such  data  helps  ensure  that workers  complete  their  jobs  free  of  any  physical  or mental  impairment  such  as drugs,  said  Neil  Sheehan,  commission  spokesman.  Twice  a  year,  each  plant  files a  report  with the  commission that  details  how many  workers tested  positive  for legal  or  illegal  substances. Continued on the following page...The  commission  examines the  data  for trends  in  drug  use  among  plant

workers,  Sheehan  said.  “It  acts  as  a  performance  indicator  of  a  plant,”  he  said.

If  a  plant  reports two  or more fitness-for-duty  program failures, the NRC

will  increase  its  level  of  oversight. An  example  of  a  program  failure  could  be  a  worker  and  plant  physician working  together  to  falsify  screening  results.  Program  failures  could  translate into  increased  inspections  and  possible fines,  Sheehan  said.

In  2001, the  NRC  hosted  a  specific  investigation  into  whether  a  former

commission-  licensed  chief  shift  operator  at the  Nine Mile  Point  Nuclear  Station

in  New  York  had  deliberately  provided  false,  inaccurate,  or  incomplete

information  on  health  history  forms.  The  investigation  uncovered  that  the

operator  deliberately  failed to  provide  complete  information  on the  forms  in

order to mislead  an  officer.

The fitness-for-duty  violation  case did not  result in  a fine,  but the NRC

could  have  issued  a  base  civil  penalty  of  $55,000.

Neither Peach Bottom nor TMI Unit  1 has been  cited for  a fitness-for-duty

violation.

- Test  limits

Rather than  have  a  zero-tolerance  drug  policy, the  NRC  relies  on  cutoff

levels to test if  a person has  abused drugs or  alcohol. For  example, the NRC’s limit

on marijuana  is  100  ng/ml  ˜  about the  equivalent  of  smoking  one  joint  in  a

week. At those  levels,  it  is  possible that  a  worker  could  endanger  himself, fellow

employees  and  the  community,  said  Jim  Beek,  a  public  information  officer  for

the  Substance  Abuse  and  Mental  Health  Services  Administration.

Continued on the following page...A  division  of the  U.S.  Department  of  Health  and  Human  Services, SAMHSA  sets  guidelines for workplace drug testing for the NRC. The level  of impairment  depends  heavily  on  a  persons  sensitivity  to  a  specific  drug,  Beek said.  Since  most  ‘street  drug’  like  marijuana  and  cocaine  are  not  regulated  by the U.S. Food  and Drug Administration, it  can  be  difficult for  experts to

determine the  strength of the drug, Beek  said.  “When  someone takes  a hit off of  a

joint,  you  don’t  know  how  or  when  it might  affect them,”  he  said.  “They  could

end  up  losing  an  arm  or  blowing  up  Delta,  Pa.”From her living  room, Marianne Adamski of Goldsboro has  a  view of TMI’s water  cooling towers  billowing  steam.  She  said the  lack  of  a  zero-tolerance  drug policy  for  plant  workers  is  ,  “cary.”

“They  should  regulate  it  much  better  than  that,”  Adamski  said.  “They

should  be  more  responsible  than  that.”The NRC’s use of  cutoff levels  rather than  zero tolerance is based on decades of  research,  Sheehan  said.  Studies  indicate  that  drugs  in  quantities  below  the cutoff  levels  are  not  likely to  affect  job  performance.  For  example,  a  plant employee  who must  report to  work  at  4  p.m. Monday  and  has  cocktails  Sunday night  should not  be  affected  by the  alcohol  once he  reports to the  plant,  Sheehan said.  “You might  have  a  small  amount  of  alcohol  in  your  body,  but  based  on evidence,  it  will  not  impair  your  ability  to  do  the  job  effectively,”  Sheehan  said.

One  expert  claims  a  zero-tolerance  drug  policy  does  not  account for  human

digestion  and  passive  exposure  involving  marijuana.  The  human  body  produces

alcohol as a process of digestion,  said Robert Stephenson, head of the SAMHSA

Division  of Workplace Programs. That  amount  of  alcohol is  below the level  of

impairment  but  above  zero,  Stephenson  said.

Marijuana  can  stick  to  clothes  and  hair,  he  said.

Continued on the following page...

If  a  person  walks through  a  room  where  people  are  smoking marijuana,  it

may  mean  that  they  were  exposed  to  second-hand  smoke  rather  than  ingesting

the  drug.  “Zero tolerance means that  we  won’t tolerate  one free  bite  of the  apple,”

Stephenson  said.

Another  hurdle  that  laboratories  must  traverse  in  the  quest  for  a  true

zero-tolerance  drug  test  is  technology.

Many  drug  cutoff  levels  exist  essentially to test  how  far  down the  screening

equipment  can  reach,  said  Dr.  Carla  Huitt.  “Much  of  the  equipment  can't

accurately  measure  down  to  zero,”  said  Huitt,  medical  director  of  the Industrial

Resource  Center  at Memorial  Hospital.  “Below the  cutoff  level, they  are  just

making  an  assumption  that  the  person  is  not  impaired.”

Regardless  of the  equipment,  doctors  cannot  determine  how  an  illegal  drug

will  affect  one  person  compared to the  next. Marijuana,  the  most  common  drug  found  in  plant  workers,  can  remain  in the body for up to  a month, Huitt  said.

- Fitness offenders

On  a  regional  level, most  nuclear  plant  workers  who tested  positive  for

drugs  were  short-term  contractors  who  work  the  sites  during  refueling.  Between

July  1999  and  December  2002,  91  short-term  contractors  at  Peach  Bottom

tested  positive  for  drugs. At  TMI,  45 temporary  employees tested  positive.  The

remaining  seven  workers  who tested  positive  for  drugs  at  both  power  plants  were

licensed  employees.

A licensed worker is someone who has been  certified by the NRC in their

job  and  works  at the  plant full time.

Continued on the following page...One  reason for the  unbalanced figures  could  be that Peach Bottom  has two operating  reactors that  require  double the manpower,  compared to the  needs  of TMI’s  lone  unit,  Sheehan  said.Typically,  plants  temporarily  hire  hundreds  of  short-term  contractors  for repairs  and  maintenance  when  reactors  are  shut  down  for  refueling.  For example,  short-term  contractors  have  been  involved  with  the  installation  of  a reactor  vessel  head  at  TMI  since  Oct.  18.  The  plant’s  unit  1  reactor  is  currently shut  down.“There  really  is  no  need to  keep  a  staff that  size  on  permanently,”  said David A.  Lochbaum,  of the  Union  of Concerned  Scientists  in Washington,  D.C.,  a nonprofit  environmental  group.

Power  companies  have  the  month-long  outages  every  two  years  to  conduct

inspections,  change  out  spent  fuel  rods,  upgrade  equipment  and  perform

preventive  maintenance  that  is  difficult  to  complete  while  a  plant  is  operational.

Since  1990,  when  the  average  refueling  outage  lasted  60  to  75  days,  the

industry  has  pushed to  reduce the  number  of  days the  power  plants  are  down,

Lochbaum  said. The more time  a  reactor is  offline, the  longer  a  plant  goes

without  supplying  power  to  the  electrical  grid  ˜  its  main  business.  “They  make

their  money  when  the  plant  is  running,”  Lochbaum  said.  “Plant  operators  began

to  hire  additional  workers  to  get  the  required  repairs  completed  in  half  the  time.”

But more  workers means more  drug  screenings  and  a  greater  potential  for

positive  chemical  tests,  Lochbaum  said.

Most of the workers who fail the plants' drug tests  are new hires who  are

screened for the first time  and  have  not  yet  been  assigned to the  protected  area,

he  said.

Continued on the following page...For those  workers  who  actively take  drugs  and make  it to the  protected

area  of the plant,  specific  safeguards  exist to  expose that person’s habits to

s e c u r i t y .

Exelon  Nuclear  operates  a  computer  program  that  randomly  drug  tests  50

percent  of  a  plant's  staff  on  an  annual  basis,  said Hugh McNally,  regional

security  manager  for  Exelon  Generation.  The  process  deters  people  from  taking

drugs  under  the  assumption  that  a  random  test  could  take  place  at  any  time,  he

said.  For  example, the  computer  could  randomly  select  a  worker  who  was tested

for drugs on Monday to be  screened  again on Thursday of the  same week.  “I  could

be  tested  three  times  in  a  year,” McNally  said.  “Personally, I’ve  been  tested  twice

in  one  week”

As  part  of the  plant’s training  process,  new  workers  are  instructed to

recognize the  symptoms  of  narcotics  use  and must  report  any  changes  in

behavior they  notice  in  other  employees.  Failure to  do  so  could  result  in  a  worker

losing his job, McNally  said.  “If I  smell alcohol on  someone’s breath,‰ he  said,  “I

need to  report  it to my  supervisor.”

At the  drug test,  a  worker must  list  all the  prescription medications  he

may  be  taking.  The  employee  must  fill  a  container  with  urine,  McNally  said.

The  worker  is  allowed to  complete the  four-minute test  in  a  bathroom  in  private,

but the  employee  is  not  permitted to  run  any  water  or flush the toilet.  “We try to

have  a lot of  controls in place  so  a person  can’t beat the  system,” he  said. An

onsite  laboratory tests the  samples. If  a  worker’s  urine  screens  positive for  drugs,

the  plant  sends  the  sample  to  an  outside  laboratory  for  complete  verification.

Exelon temporarily  denies the  employee  access to the  protected  area  of the

plant.  Once  the  outside  laboratory  has  confirmed  the  test,  the  plant's  medical

review  officer  makes  a  final  determination.

Continued on the following page...    The  commission  requires  a nuclear plant to  restrict  a worker's  access to

protected  areas  for  at  least  14  days.  “For most  people,”  Lochbaum  said,  “that

means  they  lost  their  job.  ‘The  plant may  request  a  worker  complete  drug  and

alcohol  counseling  before  the  employee  can  return  to  the  plant.

Plant officials make the final determination whether to  reinstate the

employee’s  access to the  protected  area  or to fire the  employee, McNally  said.

Access  is  automatically  denied for three  years  if  a  person  screens  positive  a

second time,  he  said.

A failed drug test could hamper a person’s chances for a new job, Lochbaum

said.  Power  companies  enter  information  relating to the failed test  into  a

national  database  that  is  monitored  by  all  power  plants.

“It's a red flag that you lost unescorted access privileges to the plant,

“Lochbaum  said.  “If  you  violated  their  drug  policy,  you've  kissed  your  job

goodbye.”

Spike in marijuana  use

Between  July  and  December  2001,  10  TMI  workers tested  positive  for

marijuana  while  20  Peach  Bottom  emploump  since  July  1999.

By  contrast,  no  workers  at  Peach  Bottom  tested  positive  for marijuana

during the  previous  six-month  period. At TMI  Unit  1, three  people tested  positive

for  the  drug  during  that  period.

Aside  from  fall  refueling  outages  that  require  more  workers,  the  jump  in

drug  abuse  may  be  attributed  to  stress.  The  Sept.  11,  2001,  terrorist  attacks

happened  during  the  six  months  when  the  spike  occurred.

Continued on the following page...Generally,  an  unstable  political  and  economic  climate  can  elevate  stress  to the  point where  a  person  could turn to  drugs  as  a  coping mechanism,  said Helen Gyimesi,  a  drug  and  alcohol  prevention  specialist  for Memorial  Hospital.  “These are mood-altering  drugs,”   she  said.  “Working  in  a  place  like  that  after  9/11 could  be  scary”. (See May  14,  2003,  for  a  related  incident).

- The NRC will increase its inspections after four unplanned  shutdowns

of the nuclear plant’s unit 2  reactor.

By SEAN ADKINS, Daily Record staff, Saturday,

November 15, 2003

For  the  next  year,  the  U.S.  Nuclear  Regulatory  Commission  will  increase

the  frequency  of  its  inspections  at  Peach  Bottom Atomic  Power  Station’s  unit  2.

Since  October  2002,  unit  2  has  experienced  four  unplanned  reactor

shutdowns,  said  Neil  Sheehan,  commission  spokesman.  An  NRC  rule  permits  a

utility  to  have  three  unscheduled  reactor  shutdowns  within  7,000  critical  hours

of  operation  or  about  one  year, he  said.

If  a  reactor  has more than three  unplanned  shutdowns, the  NRC  bumps  its

level  of  oversight  of  the  reactor.

- Dave  Simon,  spokesman for Exelon Nuclear,  said the issue  of the

shutdowns  will  be  addressed  at  a  public meeting  slated for  next  week. Exelon

Nuclear  declared  an  unusual  event  Sept.  15  when  electrical  breakers  on  the  PJM

Interconnection  power  grid  failed  to  isolate  a  lightning  strike  in  Chester  County.

The  strike  generated  a  power  surge  on two  electrical  lines that feed  into the

plant,  forcing  the  unit  2  and  unit  3  reactors  into  automatic  shutdown.

Exelon  co-owns  and  operates Peach Bottom Atomic Power  Station  and

Three  Mile Island  unit  1  in  Dauphin  County.

Continued on the following page...On  July  22,  a  fault  in  the  main  generator  system  caused  an  automatic

shutdown  of  Peach  Bottom’s  unit  2.  The  unit’s  computerized  reactor  protection

system  received  an  over-current  signal  from  the  generator,  which  caused  a  trip

of  the  main  turbine  and  shut  down  the  unit.

On April  12, the  power  station’s  unit  2  reactor  shut  down  after  an  air  line

failure.  The malfunction  resulted  in the  closure  of  a main  steam  line  isolation

valve,  which  tripped  the  automatic  shutdown.

An  equipment  failure  that  caused  multiple  bypass  valves  to  open  Dec.  21

of last  year  also led to  an unplanned  shutdown  of Peach Bottom Atomic Power

Station’s  unit  2  reactor.

In  response to those four unscheduled  reactor  shutdowns, the NRC has

labeled  unit  2  with  a  white  performance  indicator.  A  green  indicator  is  awarded

to  reactors that  require the  basic  level  of  inspection.  The  next  level  up,  a  white

performance  indicator,  is  assigned  to  a  reactor  that  requires  extra  monitoring.

As  part  of the  additional  inspections, NRC  officials  will  examine the  unit  2

reactor  for  equipment  reliability  and  operator  performance,  Sheehan  said.

“These  shutdowns  pose no  danger to the  public,”  he  said.  Mixed findings at plant

Team   investigated Sept.  shutdown of 2 reactors

- By KRISTIN FINAN Dispatch/Sunday News

A  special team that  analyzed the  causes  of,  and  responses to,  an  automatic

shutdown  of  both  reactors  in  September  at the Peach Bottom Atomic Power

Station  reported  mixed  findings  about  the  facility's  handling  of  the  event.

The  U.S.  Nuclear  Regulatory  Commission  and  representatives  from

Exelon,  the  company  that  operates  the  plant,  presented  their  early  report  last

night to the  public  at the Peach Bottom Inn in Delta.

Lightning  struck  the  plant  on  Sept.  15  and  disturbed  the  local  electrical

grid. Because  Peach Bottom  receives  energy  from the  grid  as  well  as  provides  it,

it  shut  down  automatically  around  1:30  a.m.  when  those  power  sources  were

reduced.

The  six-person team of  specialists from the NRC  regional office will  release

a full  report  by  Dec.  18. As  it  outlined  its findings  last  night, the team  said  it

found  both  positives  and  negatives  in  the  way  the  situation  was  handled.

Ma l f u n c t i o n : The  Peach  Bottom  facility,  which  has  been  generating

electricity  since  1974,  is  on  the  west  bank  of  the  Susquehanna  River  in

southeastern  York County  and  serves  about  2.5 million  homes. It  is  one  of  17

generation  units  operated  by  Exelon  Nuclear.

A major  problem  with  the  September  shut-  down  was  a malfunction  with  a

system  backup,  said  NRC  spokesman  Neil  Sheehan.  Typically,  if  there  is  a

problem  with  a  reactor,  emergency  diesel  generators  provide  more  power.

But the  reactors  shut  off  after  an hour,  and  one  of the diesel  generators

shut  down.

Team members  said that  while the  generator's  failure  appears to  be  an

equipment  problem,  they  were  not  yet  sure  who  should  have  been  accountable.

Team  members  also  found  degraded  conditions  within  the  plant  that

should  have  been  updated  and  said  concerns  voiced  by  staff members  were  never

investigated.

Continued on the following page...They  noted  lapses  in  the monitoring  of  equipment,  procedural  problems

concerning  what  action  should  be  taken  after  a  shutdown  and  conflicts  over

which  departments  should  take  action  about  specific  issues.

"We  have  not  been  as  diligent  at  identifying  problems  and  getting  them

out on the table as we need to,"  said Rusty West, Peach Bottom  site  vice president.

"We  need to  better  understand  all the  equipment  anomalies that  we  have  and

pursue  them  with  great  vigor."

- But the team  noted that the  Peach  Bottom  staff  acted  quickly  and

correctly  determined  how  to  respond  to  the  incident,  the  team  reported.

- And  managers  have  been  diligent  about  conducting  internal

investigations  and  taking  proactive  actions  ---  such  as  cleaning  equipment  and

defining  emergency  procedures,  it  said.

But  some  audience members  said the NRC  should be doing more to prevent

future  shutdowns.

Sept.  15  was  the  plant's  fourth  automatic  reactor  shutdown  in  the  past

year.  On  July  22,  Peach  Bottom's  unit  2  reactor  lost  power  after  generator

problems.  The  same  unit  shut  down  previously  on  April  12  and  Dec.  21.

- In  response, the  NRC  recently  labeled  unit  2  a  white  performance

indicator,  meaning  it  will  be  monitored  more  closely,  Sheehan  said.

But  Eric  Epstein,  chairman  of  Three Mile Island Alert,  a  group that

monitors  local  nuclear  plants,  said the  four  shutdowns  in  a  year  are  cause  for

concern.

"You  should  be  concerned with the trend," Epstein  said.  "Any time there's  a

forced  shutdown,  it  means  the  plant's  safety  systems  are  being  challenged."

-----

THE NRC’s Inspection team found  six  “Green: violations as a result of

the  incidents.  All  six  were  deemed  Non-Cited  violations

This was the forty-third, forty-fourth, forty-fifth, forty- sixth, forty-seventh

and forty-eighth   Non-Cited  Violation since June 1998. Exelon's total cost

avoidance, i.e., “credit” for 48 Non-Cited Violations = $2,490,000.

November   25, 2003 -   NON EMERGENCY  10 CFR Section:   26.73 -

FITNESS FOR DUTY Person (Organization):   ANTHONY DIMITRIADIS (R1) Unit

SCRAM Code RX CRIT Initial PWR Initial RX Mode Current PWR Current RX Mode

2 N Y  100 Power Operation  100 Power Operation  3 N Y  100 Power Operation  100

Power Operation   Event Text FITNESS FOR DUTY NOTIFICATION DURING

- RANDOM DRUG TESTING

A  contract  employee  tested  positive  during  a  random  test.  The  employee's

access to the  protected  area  has  been terminated. Contact the HOO for  additional

details. The  licensee  has  informed the NRC  Resident Inspector.

December  17, 2003 --PEACH BOTTOM-2 WAS AT 58% POWER AND

RAMPING UP THIS MORNING FOLLOWING a  reduction yesterday to 44% power

in  order to  perform  a  planned  control  rod  pattern  adjustment,  Exelon  spokesman

Ralph DeSantis  said (NUCLEAR NEWS FLASHES )

- Peach Bottom has rough week BY REBECCA J. RITZEL

Intelligencer Journal Staff

December 22, 2003 - Peach Bottom Atomic Power Station  got  a double

dose  of bad news last week. On Wednesday  a  routine test went  awry,  and  on

Thursday  a  report  arrived  in  the  mail  warning  that  plant  operator  Exelon

Nuclear  likely  will  be  cited  for  five  safety  violations  for  reactor  shutdowns  in

September.  On  Tuesday,  plant  operators  ran  a test  on the  Unit  3  reactor's

high-pressure  coolant  injection  system.  A  turbine  exhaust  valve  stuck  open

longer  than  expected,  prompting  workers  to  cancel  the  test  midway  through,

according  to  a  Nuclear  Regulatory  Commission  report.  Exelon  Nuclear  reported

to the NRC that the  plant  was  in  "accident mitigation"  status. The NRC  classified

the  valve  problem  as  a  "non-emergency  event."

Also  last  week, the  NRC  released  a  report  concerning the  September

reactor  shutdowns  at  Peach  Bottom.  Both  active  reactors  went  off-line

Sept.  22  after  a  lightning  strike  in  Chester  County  caused  widespread

power  outages.  An  NRC  inspection  team  visited the  York  County  plant  after the

incident. In  a  38-page  letter to Exelon CEO  Jack  Skolds,  an NRC  deputy  director

of  reactor  safety  detailed  results  of the  inspection.  The  inspectors  determined

Exelon  workers  responded  "adequately"  to  the  emergency.  "Nevertheless,"  the

report  says,  "the  operators  were  challenged  by  equipment  and  procedural

problems."Exelon  likely  will  be  cited for five  safety  violations  as  a  result those

problems. Of  chief  concern to the NRC is Exelon's failure to properly maintain its

emergency  generators  according  to  their  instruction  manuals.  One  of  the  four

generators failed  during the  power  outage.  On the NRC's  color-coded  scale,  safety

violations  are  classified, in descending order of  risk,  as  "red,"  "yellow,"  "white"  and

"green."  Exelon  likely  will  receive  a  white  violation  at  Unit  2  and  a  green

violation  at  Unit  3  for  the  generator  problems.  Exelon  has  until  Sunday

to  provide  additional  evidence  before the  NRC  considers  penalizing the

utility.  The  NRC  already  has  decided to  cite  Exelon  for three  green

violations  for  other  equipment  malfunctions  that  occurred  Sept.  22.

The  report  also  includes  results  from  Exelon's  own  investigation  into

the  lightning  strike.  PECO,  an  Exelon  subsidiary,  owns  the  power  lines

where  the  lightning  strike  occurred.  A  joint  PECO/Exelon  investigation

found  failures  in  circuit  maintenance  and  a  variety  of  problems  in  work

p r a c t i c e s .

When  the  lightning  strike  occurred,  a  circuit  breaker  failed  to  isolate

the  damaged  power  line,  cutting  off  power to more than  100,000  PECO

customers  and  shutting  down three Exelon  and  PECO  plants -  Peach Bottom,

Conowingo  (Md.)  Hydroelectric  Station  and  Muddy  Run  Pumped  Storage

Facility  in  Holtwood.

Exelon  determined  Peach  Bottom  could  have  been  isolated  from the  strike

if  power  substations  in  Nottingham  and  Newlinville  had  been  properly

upgraded  and  maintained.  Company  officials  said  those  upgrades  will  be

included  in  widespread  electrical  infrastructure  improvements.            Report: Funds set aside for nuke cleanup inadequate

By AD CRABLE, Lancaster New Era

Dec  3,  2003,  13:53  EST,   Congressional  investigators  say  utilities  are  not

adequately  setting  aside the hundreds  of millions  of  dollars needed to  clean  up

nuclear  reactors  at  Three Mile Island  and  Peach Bottom  when the  plant  sites

close.

The  report  by  the  U.S.  General  Accounting  Office  claims  that  funds  that,

by  law, must  be  set  aside for  restoring  plant  sites to their  original  condition may

be  as much  as 25 percent lower than needed for TMI's Unit 2  reactor.

Decommissioning for Peach Bottom's  closed Unit  1  reactor  appears to be  51 to  100

percent  underfunded,  according  to  the  report.

The  cost  of  closing down  and  removing TMI Unit  2 was  estimated  at $433

million  in  1997.  The  cost  of  decommissioning  Peach  Bottom  Unit  1  was  recently

estimated  at  $129  million  by  plant  owner  Exelon  Nuclear.  The  report  did  not  say

how much  actually  had  been  set  aside to  date  in the  decommissioning funds for

the  two  reactors.

However, the  owners  of the two  plants,  where  other  reactors  remain  in

use,  said  today  that  the  decommissioning  funding  report  by  the  investigative

arm  of Congress  is flawed  and that the money  will  be there  when the  plant  sites

end their  useful  life  several  decades  from  now.

Updating  a  1999  report  that  first  warned  that  decommissioning  funding

at many  U.S.  nuclear  plants  was  not  adequate, the  GAO  said  on Monday that the

$27  billion  saved  by  the  nuclear  industry  through  2000  was  actually  ahead  of

s chedul e .

But  breaking  down  the  savings  by  individual  plant  owners,  the  study  said

that  owners  of  42  of the  125  nuclear  plants that  have  operated  in the  United

States  had  accumulated fewer funds than  needed to  be  on track to  pay for

eventual  decommissioning,  after  the  plants  close.

Continued on the following page..."Under  our most  likely  assumptions, these  owners  will  have to  increase the

rates  at  which  they  accumulate  funds  to  meet  their  future  decommissioning

obligations,''  the  55-page  report  said.  Furthermore,  the  report  criticized  the

federal  Nuclear  Regulatory  Commission  --  the  nuclear  industry's  governmental

watchdog -- for not taking  action to force utilities to  step up funding to  address

inadequac i e s .

In  1988,  the  NRC  began  requiring  owners  to  certify  that  sufficient  money

would  be  available  when  needed  to  decommission  their  nuclear  plants.

Beginning  in  1998,  utilities  were  required  every  two  years  to  show  how  much

money  had  been  set  aside  and  where the money  was  coming from. Most funds

come  from  ratepayers  and  investments  in  trust  funds.

The  GAO  study  singled  out Exelon Nuclear, the  owner  of Peach Bottom  and

the  active  reactor  at  TMI,  as  being  behind the  curve  on  set-aside funding.  GAO

said the trust funds for  11  of the  20  nuclear  power  plants  owned  by the  company

were  inadequate.

However,  the  GAO  found  that  Exelon  Nuclear  was  actually  well  above

other  utilities  in  saving for the future  closure  of  TMI's  active  Unit  1  reactor  and

Peach Bottom's two  active  reactors. And Exelon  spokesman Craig  Nesbit  said the

more-than-adequate  funding  will  take  care  of  any  deficiency  for  the  other  Peach

Bottom  reactor  that  closed  in  1974.  Nesbit  criticized  the  GAO  report,  saying  it

looked  only  at  individual  units  instead  of  entire  plant  sites,  and  did  not  consider

specific  decommissioning  strategies,  such  as  Exelon's.

- He also said the GAO study was  "skewed'' because it did not take into

account that most  nuclear  plants,  such  as  Peach Bottom  and  TMI,  will  be

relicensed  for  another  20  years,  which  gives  utilities  more  time  to  save

decommissioning funds.  "All  of Exelon's  plants  are  adequately funded for

decommissioning  now,  and  will  be  in the  future,''  Nesbit  said.

Continued on the following page...Though  Exelon  owns the  site, the  responsibility  for  decommissioning the

TMI  Unit  2  reactor,  closed  since  a  1979  accident,  lies  with  FirstEnergy  Corp.,

which  bought  out former  TMI  owner  GPU.

The  GAO  study  indicated  the  funding  shortage  is  between  1  percent  and  25

percent for TMI's Unit  2.   FirstEnergy  spokesman  Scott  Shields  denied today that

there  were  inadequate  funds  for  restoring the  Unit  2  site to  its  original  condition.

"We will  continue to  collect funds for the decommissioning for Unit 2  and we will

be fully funded by the time the plant is  retired,'' he  said. Shields noted the  site

can't be  cleaned up until Unit  1 is  closed. TMI's license  expires in 2014 but  an

extension  is  expected. Eric Epstein,  an  expert  witness  on  decommissioning  before the Pennsylvania  Public  Utility  Commission  and  chairman  of  TMI-Alert,  a  safeenergy  citizens  group,  is  not  so  confident. He  said the GAO  study on decommissioning  shortcomings is just the tip of the  iceberg. Citing the  escalating  costs  of  disposing  of  low-level  and  high-level nuclear  waste,  Epstein  said  "clearly  the  utilities  underestimate  and  lowball decommissioning  costs.'' Epstein fears  utilities  will  not  be making the  profits  in the future when plants  are  closed down  and will not be  able to pay for what it will  actually  cost to  restore  nuclear  plant  sites.  People  not  yet  born may  have to pay  for  that  shortcoming  through  higher  electric  bills,  he  said.

Inadequate  funding  for  future  closures  was  a  constant  concern  expressed

by  former  Lancaster  mayor  Art  Morris  when  he  chaired  a  citizens  advisory  panel

on the  cleanup  of TMI in the  1980s."It's  just the  same  old  story. It's  absolutely  remarkable that  after  all these years  of  public  comment  and  criticism  that  the  Nuclear  Regulatory  Commission just  sits  and  does  nothing  about (inadequate funding),'' Morris  said today.  "The taxpayers will have to pay for it. There needs to be  an NRC that  stays on top of  this  and monitors  it.''

December 22, 2003 - NATIONAL GUARD TROOPS BEGAN PROTECTING

PENNSYLVANIA'S NUCLEAR POWER PLANTS  at  7  a.m.  local time today,

according to Gov. Edward  Rendell (D). Troops will  remain  at the  plants  as  long  as

the  threat  level  remains  at  "orange,"  indicating  a  high  risk  of  a  terrorist

incident,  Rendell  said.  Deployment  of  the  state  National  Guard  to  the  nuclear

plants  was  among  the  steps  the  state  government  took  to  protect  Pennsylvania

infrastructure  in  response  to  the  raising  of  the  Homeland  Security  Threat  Level

yesterday.  The  nuclear  plants  in  Pennsylvania  are  Beaver  Valley,  Limerick,

Peach  Bottom,  Susquehanna  and  Three Mile Island.  NRC  spokesman  Dave

McIntyre  said  he  was  not  aware  of  other  states  deploying  National  Guard troops

to  nuclear  plants  in  response to the  increased threat  level (NUCLEAR NEWS

FLASHES.)

- NEW YORK,

- Jan  13, 2004 (Reuters) - Exelon Corp., the No.  1 U.S. nuclear plant

operator,  on  Tuesday  said  it  named  nuclear  industry  veteran  Christopher  Crane

as  chief  nuclear  officer  and  president  of  its  key  nuclear  division.  Crane  replaces

John  Skolds, who was named president of Exelon's  energy delivery unit --  a

position  left  vacant  by  the  resignation  of Michael  Bemis.

Jan  13,  2004  Reuters

Power News Sat,

Jan. 17, 2004    Authorities:  Pilot  who  buzzed  area  was  drunk

- By NICOLE WEISENSEEEGAN

The  pilot  who  terrorized  the  airways  with  his  erratic  flying  for  four  hours

- Thursday  night  -  circling  the  Limerick  nuclear  plant  and  buzzing

Philadelphia  International  Airport  -  was  drunk,  authorities  said  yesterday.

When  he  emerged  from  his  single-engine  plane,  he  was  staggering,  his  eyeswere

bloodshot,  and  his  pants  were  unbuttoned  and  unzipped,  authorities  said.

Tests  showed that the  pilot,  John  Salamone,  owner  of  a  Pottstown  concrete

company,  had  a  blood-alcohol  level  of  0.13,  over the  legal  limit  of  .08.  Until tests

are  complete,  however,  he  has  not  been  charged  with  DUI,  according to

Montgomery  County  District  Attorney  Bruce  L.  Castor  Jr.  Salamone,  44,  owner

of  J. Vincent Concrete Contractors  ,  was  released  into the  custody  of  his  brotherin-law.  The  single-engine  plane  he  was  flying  is  registered to  his  firm,  records

show.

Jim  Peters,  a  Federal  Aviation  Administration  spokesman,  said  his  agency

had  opened  an  investigation  into  Salamone  but  have  not  yanked  his  license.

"At the  end  we  will make  a  recommendation  about  what to  do,"  he  said. That

could  mean  anything  from  no  action  to  a  civil  penalty,  or  suspension  or

revocation  of  his  license.  Salamone  did  not  return  phone  calls  requesting

c o m m e n t .

Salamone  took  off  from  Pottstown-Limerick  Airport  between  6:15  and  6:30

p.m.,  Peters  said.  He  first  flew  over  Center  City, then  headed toward

Philadelphia  International  Airport,  prompting  controllers  to  order  six  aircraft

that  were  on final  descent to  clear  out  of the  way, Peters  said.

Salamone  then  headed  to  South  Jersey  and  attempted  tried  to  land  at  an

airport  outside  Glassboro  before  returning  to  Philadelphia  airspace.

He  declined to  land  in  Philadelphia,  and then  headed to  Limerick,  where

he  landed  briefly  there,  before  taking  off  toward  the  nuclear  plant.  He  finally

landed  again  at  Limerick  airport  and  was  arrested,  authorities  said.         York Daily Record: NRC watching Peach Bottom -

- The power station was issued violations after a September

reactor  shutdown.

By  SEAN ADKINS Daily  Record  staff Tuesday,

February  10,  2004 - The  U.S.  Nuclear  Regulatory  Commission  will  be  more vigilant  of Peach Bottom Atomic Power Station’s Unit  2  reactor  as  result  of  a  second-tier safety  violation. The  commission  has  penalized  the  Unit  2  reactor  with  a  “white” finding  related  to  the  failure  of  an  emergency  diesel  generator  during  an

unscheduled  Sept.  15  reactor  shutdown. A white  violation  refers to  an  event  at the plant that is  considered  as  of low to  moderate  safety  significance.

Since the  generator failure  affected  both  of the  plant’s  units,  NRC  officials

tacked  on  a  green  violation  in  regard to the  power  station’s  Unit  3  reactor.

A  green  violation  is  an  event  characterized  as  being  of  very  low  safety

significance,  said  Neil  Sheehan,  spokesman  for  the  NRC. The  commission  decided  on  a  green  violation  because  fewer  safety-related electrical  loads  powered  by  the  emergency  generator  exist  for  Unit  3.“This will help us better  know where we need to focus  an increased level  of attention  going  forward,”  Sheehan  said.

A  bolt  of  lighting  struck  a  Chester  County  power  pole  Sept.  15,  generating

an  electrical  surge  along  power  lines that feed  into  Peach Bottom Atomic  Power

S t a t i o n .

The  strike  led  to  the  automatic  shutdown  of  the  plant,  which  triggered  the

formation  of  a  special,  augmented  NRC  inspection  team.

As  part  of  its  findings,  the  team  found  that  faulty  protection  circuitry  and

a  loose  wire failed to  contain the  surge that  disabled the  plant.

Exelon  has  replaced  all  damaged  fuses  and tightened  necessary  wires to

help  ensure  a  similar  event  will  not  shut  down  the  power  station.

- Within moments  of the  September  shutdown, the  plant’s  four  diesel

generators  kicked  on to  power the  station’s  vital  equipment  and  offices.About  an  hour  later,  one  of the  reserve  generators  seized. Exelon  declared  a

“discretionary”  unusual  event  —  the  lowest  of  the  NRC’s  emergency  categories.

“This  is  not  a  common thing,”  Sheehan  said.  “These  generators  should

operate  smoothly.”

The  commission’s  inspection  team  found  that  deficient  procedures  were

followed  during  the  1992  installation  of  generator  adapter  gaskets.  Combustion

gas  leaked into the jacket water  cooling  system —  a  problem that  led to the

automatic  tripping  of  the  generator  Sept.  15.

In March  and April  2003, Exelon took  corrective  actions to  repair the

observed  low  jacket  water  pressure  conditions.  The  NRC  said the...problem  was

not  resolved.

- Last  June,  commission  inspectors  documented  that  lube  oil  had

leaked from  loose flange  joint  bolts  on  an  emergency  diesel  generator  at the

plant.  That  leak  caused  a  small  fire  in  the  exhaust  manifold  during  a  test.

The NRC  responded to the fire  by  issuing  a  green  violation.

Exelon  has  less than  a month to  reply to the  commission’s  white finding.

The  company  will  not  appeal  the  determination,  said  Craig  Nesbit,  a  company

spokesman.

Exelon  agrees  with the  NRC’s findings,  he  said.

- February 22, 2004 Event  Text

- MANUAL SCRAM AT PEACH BOTTOM 2 DUE TO

- DECREASING CONDENSER VACUUM

"Peach  Bottom  Unit  2  reactor  was  manually  scrammed  due  to  degrading

main  condenser  vacuum.  The  reactor  was  manually  scrammed  prior  to

reaching  the  automatic  scram  setpoint.  All  plant  systems  responded  as  expected

with no  significant  issues  noted. A  Group II  and  Group III Primary Containment

Isolation  was  received  due  to  reactor  water  level  passing  through  1  inch.  All

isolation  systems  responded  as  required  and  repositioned to their  expected

positions."   The licensee  also indicated that  all  control  rods properly inserted into

the  core.  The method  of  decay  heat  removal  was  using the main  condenser.  The

licensee  initiated  a  post  scram  review to  identify  and  correct the  source  of

degrading  vacuum.  The  licensee  also  indicated  the  manual  scram  was  initiated

at  25  inches  and  lowering  of  condenser  vacuum.

The licensee notified the NRC Resident Inspector.YDR: Reactor shutdown no threat -  Mechanical problems  caused Peach Bottom’s

Unit 2 reactor to be shut down Sunday.

- By  SEAN  ADKINS  Daily  Record  staff Wednesday,

February  25,  2004 -Operators  manually  shut  down  Peach  Bottom  Atomic  Power  Station’s  Unit 2  reactor  Sunday  after  a  series  of  mechanical  problems.

Last  week,  control  room  workers monitored  an  air  leak  in the  reactor’s

condenser  —  equipment  used  to  turn  steam  into  water. The condenser  pumps  that  water  back  to  the  reactor.

On  Tuesday,  plant  officials  determined  the  leak  came  from  an  expansion

joint  caused  by  routine  wear  and tear  of the  system,  said  Dana Melia,

spokeswoman for Exelon Generation. Exelon  co-owns  and  operates the power

stat ion.“That  type  of  wear  and  tear  is  typical  of  any  steam  plant,” Melia  said.

That leak  caused  a loss of  vacuum —  a piece of  equipment found inside the

condenser,  she  said.

The  shutdown  caused  no threat to  public  health  or the  plant’s  ability to

distribute  electricity,  Melia  said.

- Peach Bottom Atomic Power  Station’s Unit  3 was not  affected  by its

neighbor’s  shutdown  and  continues  to  function  at  full  power.

The  second unit’s  reactor is designed to  go into  automatic  shutdown if the

vacuum  level  drops to  a  specific  set  point, Melia  said.

On  Sunday,  operators  elected  to  manually  take  the  reactor  offline  and

bring the  unit to  a  cold  shutdown.“(A  shutdown)  is  safer  when  it’s  manual  rather  than  automatic,”  Melia said.  “You  have  more  control  over  it.”All  equipment  used to  carry  out the  shutdown  functioned  as  it  should, Melia  said.“They  did  what they  were  supposed to  do,”  said  Diane  Screnci, spokeswoman  for  the  U.S.  Nuclear  Regulatory  Commission.  “The  plant’s  systems responded  as  expected.”Soon  after the  3:11  p.m.  shutdown, the  plant  notified  its  resident  NRC

inspector  of the  unit’s  problems.

The  commission is having its inspector  look into the  cause  of the  shutdown,

Screnci  said. As  for  Exelon,  officials  are  investigating the  cause  of the  leakage  and  what steps  are  necessary to  bring the  plant’s  second  reactor  back  online, Melia  said.

“We  are  trying  to  determine  why  it  happened,”  she  said.

Plant  officials  will  use the  shutdown  as  an  opportunity to  conduct  routine

maintenance  of  the  site  such  as  the  checking  of  valves.

While Melia  did  not  say  when the  reactor  would  return to  service,  Screnci

said  the  time  frame  is  more  “a  matter  of  days  rather  than  months.”

- YDR: NRC still watching Peach Bottom -

Four unplanned shutdowns in about a year netted the reactor a ‘white' violation,

which gets it extra oversight.

By  SEAN  ADKINS  Daily  Record  staff  Saturday,

April  10,  2004 -At bottom: · IF YOU GO A low to moderate  safety  violation discovered last  year means  additional  regulatory  oversight  for  Peach  Bottom  Atomic  Power  Station's Unit  2.

The unit will face  a Nuclear Regulatory Commission  supplemental

inspection  later this  year  as  a  result  of  deficient  performance  based  on  its

number  of  unplanned  shutdowns.

The commission will follow a normal inspection schedule for the power

station's third  unit through  Sept.  30,  2005. Based  on the  assessment  of  an NRC

inspection team, the  commission  cited  Unit  2  with  a  "white"  violation for the

failure  of  the  emergency  diesel  generator.

Following a Sept.  15 unplanned  shutdown of Units 2 and 3, a  reserve

generator  seized.

The generator, one of four, helps power the plant's vital equipment and

Offices.  A  commission inspection team later found that deficient procedures were

followed  during  the  1992  installation  of  generator  adapter  gaskets.  Gas  leaked

into the  equipment's  jacket  water  cooling  system —  a  problem that  led to the

automatic  tripping  of  the  generator  Sept.  15.  The  NRC  team  determined  that

corrective  actions  Exelon took to  repair the  observed  low  jacket  water  pressure

conditions  in March  and  April  2003  were  inadequate.  The  problem  was  not

r e sol v ed.

Since that time, the plant has  created  corrective  actions to  ensure the

operation  of the  generators,  said Pete  Resler,  spokesman for Exelon Nuclear,

which  co-owns  and  operates the  power  station.

For  example, the plant has  revised maintenance, testing  and inspection

procedures  for  the  diesel  generators.

Training materials  regarding the  generators  have  been  updated,  Resler  said.

Aside from the low to moderate  safety breach, five  "green" violations at Unit

- 2  in  2003  caught  the  attention  of  the

commission.

A  green  violation is  characterized  as being  of  very low  safety  significance.

Some of the green infractions include problems with the second unit's safe

shutdown  emergency  lights  and  the  emergency  diesel  generator  fire  protection

system.  "These findings  highlight  a  need for Exelon to  improve this  area,"

according to  a March  3  letter  sent  by the  NRC to the  utility.

Commission officials will make another trip to Peach Bottom Atomic Power

Station's  Unit  2  in  September to  review the  causes  behind the  reactor's four

unplanned  shutdowns  per  7,000  critical  hours,  or  roughly  one  year  of  operation.

The shutdowns occurred between the fourth quarter of 2002 and the fourth

quarter  of  2003,  said  Diane  Screnci,  spokeswoman  with  the  NRC.

The fourth shutdown that occurred during the third quarter  of 2003 netted

the second  reactor  a  white  performance  indicator,  she  said.

_____

Increased  oversight  was maintained  by  the  NRC  at  Peach  Bottom-2,  “which  will

face  a  Nuclear  Regulatory  Commission  supplemental  inspection  later  this  year

as a result of deficient  performance based on its number of unplanned

shutdowns.  The  commission  will follow  a  normal  inspection  schedule for the

power  station's third unit through Sept. 30, 2005   (York  Daily  Record.)        Unplanned shutdowns and equipment failure were to blame.

- By  SEAN ADKINS  Daily  Record  staff Thursday,

April  15,  2004 -With  little more  than  a  projection  screen  between  them,  officials  with  both the  Nuclear  Regulatory  Commission  and  Exelon  Generation  met  Wednesday night  at  the  Peach  Bottom Inn  to  walk  through  the  agency's  annual  safety performance  assessment  of  Peach  Bottom  Atomic  Power  Station.

Based on a 2003 low-to-moderate  safety violation,  commission officials will

host  a  supplemental  inspection  of Unit  2 to  ensure the  reliability  of the  plant's

diesel  generators.

In September, NRC  staff will investigate through  an  additional inspection

the  reason  behind  Unit  2's  four  unplanned  shutdowns  per  7,000  critical  hours,

or  roughly  one  year  of  operation.  The  unscheduled  shutdowns  occurred  between

the  fourth  quarter  of  2002  and  the  fourth  quarter  of  2003.

The fourth  shutdown that occurred during the third quarter of 2003 netted

the  second  reactor  a white performance indicator —  a  violation  of low to    safety

s igni f i canc e .

Between Jan.  1 and Dec. 31, 2003, both Peach Bottom Atomic Power

Station's  Unit  2  and  3  reactors  racked  up  17  green  violations —  an  infraction  of

very  low  safety  significance,  said  Brian  Holian,  deputy  director  of  reactor

projects   for the NRC's Region 1.

Some of the green infractions include problems with the second unit's safe

shutdown  emergency  lights  and  the  emergency  diesel  generator  fire  protection

system.   "Seventeen  green  violations,"  Holian  said,  "it's  a  hefty  amount.  But  you

have to  remember  it's  a twin  reactor  plant  and that's  for  both  units."

Bill Levis, vice president of mid-Atlantic operations for Exelon, said the

company  views  the  violations  as  an  indicator  that  the  plant  did  not  meet

expectations.  “We  can  clearly  do  better  than  that,"  he  said.

The commission will follow a normal inspection schedule for the power

station's  third  unit  through  Sept.  30,  2005.

On Sept. 15, one of the plant's four emergency diesel generators seized. The

equipment's  failure  occurred  in  the  hours  following  an  unplanned  shutdown  of

both  reactors.

A  commission inspection team later found that deficient procedures were

followed  during  the  1992  installation  of  generator  adapter  gaskets.         Gas leaked into the equipment's jacket water cooling  system — a problem

that  led  to  the  automatic  tripping  of  the  generator.

Typically, the plant  runs all four diesel generators for at least two hours

every  two  weeks  to  check  for  reliability,  said  Craig W.  Smith,  senior  resident

NRC  inspector  at  Peach Bottom Atomic  Power  Station.  The  NRC team  determined

that  corrective  actions  Exelon took to  repair the  observed  low  jacket  water

pressure  conditions  in March  and  April  2003  were  inadequate.  The  problem  was

not  resolved.

"We didn't do enough fast enough," Levis said. "We recognize our obligation to

public  health  and  safety.  We  take  that  very  seriously."  Since  the  generator

failure,  the  plant  has  instituted  a  monitoring  system  that  tracks  the  amount  of

gas that  could  leak  into the  generator's  cooling  system,  said  Paul  Davison,

director  of  engineering  for  the  power  station.

Following the failure, the plant  checked  all the  generator  adapter  gaskets

and  installed  new  equipment  as  needed,  he  said.

Other tests that were in place prior to the generator  shutdown  scan for

temperature,  engine  reliability  and  vibration  control.

"We will follow all this up with inspections," Holian said. "The proof will be in

the  pudding."

- July  2,  2004:

- GOVERNOR RENDELL ANNOUNCES ENHANCED SECURITY

- MEASURES AT NUCLEAR POWER PLANTS

National Guard, State Police to Provide a 24-hour Presence and

Random, Unannounced Patrols During Independence Day Holiday

HARRI SBURG: Governor Edward  G.  Rendell today  said the Pennsylvania

National  Guard  and  the  Pennsylvania  State  Police  will  provide  both  a  24-hour

presence  and  random,  unannounced  security  patrols  at  the  Commonwealth’s

five  nuclear  power  plants.   The  enhanced  security  measures  will  be  provided  in  a

coordinated  fashion  with  the  plant  operators  and  their  security  teams,  and  will

remain  in  force  at  least  through  the  conclusion  of  the Independence  Day  holiday.

“My  Homeland  Security  Team  continues  to  coordinate  on  a  regular  basis

with  the  U.S.  Department  of  Homeland  Security,  the  Federal  Bureau  of

Investigation,  the  U.S.  Department  of  Defense,  and  the  Nuclear  Regulatory

Commission  in  order  to  discuss  and  share  relevant  intelligence  information  and

threat  analysis,”  Governor  Rendell  said.“Although  there  currently  exists  no  credible  threat  against  any

Pennsylvania  nuclear  power  facility,  in  an  abundance  of  caution  I  have  asked

the  National  Guard  and  State  Police  to  immediately  commence  enhanced

security  measures  at  our  nuclear  power  stations.  At  a  minimum,  we  will

maintain  this  deployment  status  through  the  holiday  weekend.”

The  state’s  nuclear  power  plants  are  Beaver  Valley  in  Shippingport

Borough,  Beaver  County;  Susquehanna  in  Salem  Township,  Luzerne  County;

Limerick  in  Limerick  Township,  Montgomery  County;  Peach  Bottom  in  Delta

Borough,  York  County;  and  Three Mile Island  in  Londonderry  Township,

Dauphin  County.

- Groups want action on nuke fuel storage

Watchdogs prod federal  regulators to  shore up  spent-fuel pools against possible

terrorism.  Peach  Bottom  is  among  plants  affected.

August 11, 2004

Day: Wednesday     Page: B-1        Byline: Ad Crable

LANCASTER NEW ERA  - Used,  deadly  uranium fuel  stored  at the Peach Bottom

and  31  other  similarly  designed  nuclear  reactors  around  the  United  States  is

especially  vulnerable  to  terrorist  attack,  watchdog  groups  charge.  "Nuclear

reactors  are  pre-deployed  weapons  of mass  destruction,"  said  Deb Katz,  executive

director  of Citizens Awareness Network,  one  of three-dozen  public  interest  groups

signing  the  petition,  including  Greenpeace,  Union  of  Concerned  Scientists  and

the  locally  based  Three Mile Island  Alert.

The  groups  filed  a  petition  for  action  with the  U.S.  Nuclear  Regulatory

Commission,  calling  on  the  agency  to  immediately  address  structural

vulnerabilities to terrorism  at the plants.   "It is the NRC's job to protect our

health  and  safety  and  assure  public  confidence  in  the  regulatory  process.

Presently, NRC's  efforts  are inadequate,"  said Eric Epstein  of TMI Alert  and  a

candidate  for  the  state  Senate. While  alleging  that  all  103  commercial  nuclear  plants  in  the  country  are vulnerable to  accidents  or  "acts  of malice  or  insanity," the  33-page  petition particularly  points the finger  at  spent-fuel  pools  at Mark I  and II  boiling  water reactors,  such  as  that  found  at  Peach  Bottom.

At those nuclear plants, used uranium fuel  rods  are placed in pools  of

water  high  above  the  ground,  covered  by  only  a  lightweight  roof  and  walls,  the

groups  say.   The  arrangement,  they  say,  makes  the  pool  vulnerable  to  terrorist

attacks from planes or on the ground.    "If a pool is breached, there is no

surrounding  structure  or  backfill  to  inhibit  the  drainage  of  water. Its  cooling

system  is  vulnerable  to  attack  at  several  points.  The  exterior  configuration

of  the  reactor  building  facilitates  accurate  aiming -  for  example,  of  an  explosiveladen  aircraft  -  by  a  knowledgeable  attacker,"  the  petition  states.

- The  group  says breaching  of  spent-fuel pools  "could  cause  great

public  harm"  with  widespread  radiation  fallout.

The groups outline a number of  steps they feel the NRC  should take,

including  beefing  up  on-site  security;  re-equipping  spent-fuel  pools  with  lowdensity  racks  so that  spent fuel would not ignite if water were lost from the pool;

establishing  ways  to  recover  from  loss  of  water;  and  improving  emergency

response  plans  for  surrounding  communities.

The  petition  comes  shortly  after  concerns  about  spent-fuel  vulnerability

were  voiced  by  some members  of Congress.

Craig Nesbit,  spokesman for  Peach Bottom  operator Exelon Energy,  said

this morning  that  "there  is  nothing  substandard  about  any  of  Exelon's  plant

designs."

The NRC  has no  comment  on the  petition  while the  agency  is  processing

it to  see if it meets the NRC  standards for  action,  spokeswoman Diane Screnci

said.

A  spokeswoman  for  the  Nuclear  Energy  Institute,  a  nuclear  industry

group,  said  she  had  not  yet  seen the  petition.

In  another  development  affecting  Peach  Bottom,  the  federal  Department

of Energy  announced  it  would  pay Exelon  at  least $300 million for  costs

associated  with  storage  of  spent  fuel  at  its  nuclear  plants.

The DOE had promised in the  early  1980s to  accept used fuel from U.S.

reactors  for  disposal,  beginning  in  1998.  Amid  extensive  controversy,  however,

a  national  repository  has  not  yet  been  built. Exelon  and  64  other  companies  sued

DOE for not taking the fuel.    By  SEAN ADKINS  Daily  Record/Sunday News,

September  1, 2004 -The  Nuclear  Regulatory  Commission  has  requested  that  officials  at  Peach Bottom Atomic Power  Station Unit  2  submit  in  writing  plans   to  address inadequate  corrective  actions  for  known  equipment   problems.

The cross-cutting issue includes two  "green" violations of very low  safety

significance  listed  within  the  commission's  mid-cycle  performance  review  and

inspection  plan  of the  power  station.

That  review  stretched from  July  1, 2003, to  June 30. The NRC  released the

review  Monday.

Next month, a team from the NRC will travel to the plant to  run an

additional inspection on Unit 2 to determine how Exelon has  responded to  "white"

performance  indicators  found  in  the   third  quarter  of  2003  and  the  first  quarter

of  2004.

Exelon co-owns and operates Peach Bottom Atomic Power Station.

The power station's Unit 3 performance requires no   additional NRC

oversight.  That  unit  will  follow  a  normal   inspection  schedule  through  March  31,

2 0 0 6 .

The  supplemental inspection will investigate the  reason behind Unit 2's four

unplanned  shutdowns  per  7,000  critical  hours,  or  roughly  a  year  of  operation.

- The unscheduled  shutdowns occurred between the fourth

quarter  of  2002  and the  fourth  quarter  of  2003.  One  of the  unplanned

shutdowns  included the failure  of  one  of the  plant's four  emergency  diesel

generators.   Following the shutdown,  a  commission  inspection team   found that

deficient  procedures  were  run  during  the  1992  installation  of  generator  adapter

gaskets.  Gas leaked into the  equipment's  jacket  water  cooling  system —  a  problem

that led  to  the  automatic  tripping  of  the  generator.

The NRC determined that the problem warranted a  "white" finding, or a

violation  of  low  to  moderate  safety  significance.

Earlier this year, the plant formed a  root-cause analysis   team from the

power station's maintenance  and  engineering   divisions  to  deal  with  the  failed

diesel generator,  said  Dana Melia,  an  Exelon  spokeswoman.         The plant put its  self-critical analysis into action in   June and further

modified its plan last month,  she  said.   The actions focused  on the maintenance  of

the  generator   and  other  reliability  conditions, Melia  said.   The NRC will  look  at

all  the  plant's  actions  during  its   September  inspection.

Power station officials are now forming a second root-cause team to deal with

the  plant's  ongoing  problems  with   cross-cutting  issues, Melia  said.

Cross-cutting issues are  events that affects many different areas of plant

performance,  said  Neil  Sheehan  of the  NRC.  "The  substantive  cross-cutting  issue

was  based  on  several   inspection findings  in  which  corrective  action for  a  known

equipment  problem  was  either  insufficient  or  delayed  for   implementation,"

according  to  the  mid-cycle  review.

The most  recent findings deal with problems  related to Unit 2's high-pressure

coolant  injection  oil  system  and  high-pressure  service  water  valves,  Sheehan

said.  Both  problems  resulted  in  green  violations.

The high-pressure  coolant injection oil  system is a   reserve  safety operation

put  into  play  to  shut  down  the  plant   quickly,  Sheehan  said.

The oil is used to lubricate the  system that injects   coolant into the  reactor

vessel to keep the fuel  cool  at times of   emergency, he  said.

In June, plant officials found that oil flow to a part of   the system had been

interrupted.  As  a  result,  damage  to  the  turbine  bearing  and  rotor   rendered  the

machine  inoperable.  The  plant  had  to  replace  the   bearing  and  rotor.  The  system

was  unavailable.

The  second green violation dealt with  corrective actions   of high-pressure

service  water  valves  that  pull  water  from  the   Susquehanna  River  that  is  used  to

cool  down  various  plant   components,  Sheehan  said.

How the plant will respond to the violations will be part   of the letter sent to

the NRC in October, Melia  said.

- September  12,  2004- State plan to handle nuke crisis challenged

Preschools, hospitals and nursing homes are unprepared,  2 residents say

- BY GARRY LENTON Of The Patriot-News

State  and  federal  authorities  are  investigating  allegations  that

Pennsylvania  is  unprepared  to  evacuate  preschool  children  and  nursing  home

and  hospital  patients  during  a  nuclear  accident.

The  federal  government  requires  that  the  state  have  a  plan  for  moving

people  who  cannot  care  for themselves  and  live  within  10 miles  of  a  nuclear

plant.  Two  Harrisburg  area  residents  allege that the  state  has  been  out  of

compliance  with  federal  safety  requirements  for  nearly  two  decades.

Gov.  Ed  Rendell's  office  and  the  Federal  Emergency Management  Agency

took  on the  review  of the  state's  plan  after  receiving  a  letter  last  week from  Larry

Christian  and  Eric  Epstein,  chairman  of  the  watchdog  group  Three Mile Island

Alert,  detailing  these  issues.  The  Nuclear  Regulatory  Commission  also  received

the  letter.

If the  accusations  are  deemed true,  it  would  call  into  question the  validity

of  the  operating  licenses  for  the  five  nuclear  power  stations  in  Pennsylvania.

Federal  law  requires the NRC to  determine that the  public  will  be  protected  in  a

radiological  emergency  before  it  grants  a  license  to  open  a  nuclear  plant.

- December 22, 2004 Event  Text

REACTOR SCRAM AND ECCS INJECTION FOLLOWING OPENING

- OF TURBINE BYPASS VALVES

"At  approximately  04:55  on  December  22,  2004,  Unit  2  experienced  a

malfunction  of  Electro-Hydraulic  Control  (EHC)  system  resulting  in  opening  of

main  turbine  bypass  valves  and  resultant  loss  of  reactor  pressure.  The  reactor

automatically  shutdown  on  RPS  with the  completion  of  a  Group I  isolation  signal

(Reactor  pressure  850  prig  and  Reactor mode  switch  in  RUN)  resulting  in  a

closure  of the Main Steam Isolation Valves (MSIVs). Reactor level lowered to

(ECCS) initiation  set-point  of -48 inches  and High Pressure Coolant Injection

(HPCI)  system  and  Reactor  Core Isolation  Coolant (RCIC)  system  automatically

initiated  and  restored  level. When  reactor  level  lowered  below  the  1  inch  setpoint,  Group II  and III Primary Containment Isolation  System (PCIS)  signals

initiated.  All  Unit  parameters  are  stable  and  RPS/PCIS/ECCS  systems  performed

as  designed. MSIVs  remain  closed.  Reactor  level  and  pressure  are  stable  with

HPCI and RCIC systems in control. Group I, II, and III isolations have been reset.

The  EHC  malfunction  is  presently  under  investigation  by  Station  Management."

All  systems  functioned  as  required.  The  reactor  water  level  is  now  at  23  inches

and  stable and the licensee is  conducting a  slow depressurization to Mode 4 to

investigate  the  EHC  system  malfunction.  The  level  transients  experience  during

the  scram would be  expected with the  closure of the MSIVs.

The licensee has notified the NRC Resident Inspector.

Peach Bottom-2, already under increased NRC  supervision,

scrams again

REACTOR SCRAM AND ECCS INJECTION FOLLOWING OPENING OF TURBINE

- BYPASS VALVES

"At  approximately  04:55  on  December  22,  2004,  Unit  2  experienced  a

malfunction  of  Electro-Hydraulic  Control  (EHC)  system  resulting  in  opening  of

main  turbine  bypass  valves  and  resultant  loss  of  reactor  pressure...All  Unit

parameters  are  stable  and  RPS/PCIS/ECCS  systems  performed  as  designed...The

EHC  malfunction  is  presently  under  investigation  by  Station  Management...

The  reactor  water  level  is  now  at  23  inches  and  stable  and the  licensee  is

conducting  a  slow  depressurization to Mode  4 to  investigate the EHC  system

malfunction...The  licensee  has  notified  the  NRC  Resident Inspector.” (NRC,

Region I,Power  Reactor Event  Number:  41277.)

Continued on the following page...         By TOM JOYCE Daily Record/Sunday News

Saturday,

December  25,  2004 -Peach  Bottom  Atomic  Power  Station's  Unit  2  reactor  had  an  emergency shutdown  early  Wednesday  morning. It was down for about 48 hours, and  started up again on Friday morning, according to  Craig  Nesbit,  a  spokesman  for  Exelon, the  company that  owns the

p l a n t .

No  radiation leaked during the  shutdown, Nesbit  said. In fact, the  shutdown

didn't  occur  in  a  portion  of the  plant that  contains  radiological  parts. According

to  Nesbit,  the  problem  occurred  when  a  circuit  card  malfunctioned  in  the

electronic  hydraulic  control  system.

The plant shut down, as it's designed to do in such circumstances. Nesbit

characterized  it  as  an  engineering  issue  rather  than  a  safety  issue.

The time-consuming  part  was figuring  out  precisely  where the malfunction

occurred.   "It's  a  relatively  simple  operation,  but  it takes  a few

days,"  Nesbit  said.

The plant has  experienced  several  emergency  shutdowns in the past two

years,  Nesbit  said.  Plant  officials  are  now  conducting  a  "root  cause  investigation"

to  see  if the  problems  are  all the  result  of  an  underlying  problem,  or  simply

isolated  occurrences.   "A  root  cause  investigation  is  a  very  detailed  and

intense look at the  root  cause of the problem," Nesbit  said.

The Nuclear Regulatory Commission  could not be  reached for  comment. On

Friday,  the  Lancaster  Intelligencer-Journal  reported  that  an  NRC  spokesman

said the  commission is  concerned  about the frequency  of Peach Bottom's

shutdowns .

In August, the NRC  sent Exelon's CEO a letter warning the company to

improve  its  routine  maintenance  work  for  the  remainder  of  2004  or  face

increased  federal  oversight. And  in  September, the  NRC  sent  a  special  inspection

team to  see  what  Exelon  was  doing to  prevent  emergency  shutdowns  at  Unit  2.

- Feb. 7, 2005- Peach Bottom Unit 2 shuts down for valve replacement

Chicago-based energy company Exelon Corp.'s 1,110-megawatt Unit 2 reactor at the Peach Bottom nuclear station in Pennsylvania exited a work outage and ramped up to full power by early Monday, the U.S. Nuclear Regulatory Commission said in its power reactor status report.

The company shut the unit on Feb. 2 to replace a safety relief valve.

The 2,220 MW Peach Bottom station is located in Peach Bottom, Pennsylvania, about 75 miles southwest of Philadelphia. There are two 1,110 MW units 2 and 3 at Peach Bottom.

Unit 3, meanwhile, continued to operate at full power.

One megawatt powers about 1,000 homes, according to the North American average.

Exelon Nuclear, a unit of Exelon's Exelon Generation subsidiary, operates the station for its owners: Exelon (50 percent) and New Jersey-based energy company Public Service Enterprise Group Inc. (PSEG) (50 percent).

In December 2004, Exelon agreed to acquire PSEG. Pending regulatory and shareholder approvals, the companies expect to complete the deal in 2006.

-Report from Rueters

- Feb. 9, 2005 -Peach Bottom Unit 2 back in production

Chicago-based energy company Exelon Corp.'s  1,110-megawatt Unit 2 at the Peach Bottom nuclear station in Pennsylvania ramped up to 94 percent of capacity by early Wednesday, the U.S. Nuclear Regulatory Commission said in its power reactor status report.

On Tuesday, the unit was operating at 64 percent of capacity as it increased power following a planned control rod pattern adjustment.

The company performed the rod pattern adjustment to optimize the efficiency of the fuel in the reactor after the reactor exited an outage started on Feb. 2 to replace a safety relief valve.

The 2,220 MW Peach Bottom station is located in Peach Bottom, Pennsylvania, about 75 miles southwest of Philadelphia. There are two 1,110 MW units 2 and 3 at Peach Bottom.

Unit 3, meanwhile, continued to operate at full power.One megawatt powers about 1,000 homes, according to the North American average.

-Report from Rueters

- Feb. 11, 2005- Nuclear plant guard rule could be year away

TMI watchdog group decries 'glacier' pace The Harrisburg-based nuclear watchdog group Three Mile Island Alert has been waiting since Sept. 12, 2001, for the U.S. Nuclear Regulatory Commission to decide whether nuclear plant owners must post armed guards at their front gates.

TMIA will have to wait another year for its answer, according to an NRC memo released to Wednesday. The memo outlines a schedule the NRC plans to follow as it considers rule changes for security at the nation's 63 nuclear power stations.

The memo, from Luis A. Reyes, executive director for operations, anticipates that recommendations that could mandate guards at plant entrances will be presented to the commissioners next February.

If the NRC adheres to the schedule, the recommendation would come nearly five years after TMIA petitioned the agency for the change.

A statement issued by the watchdog group yesterday called the NRC's failure to act on its request irresponsible and unreasonable. "For nearly four and a half years the NRC has misled [TMIA] about its deliberations on the petition," the statement said. "When requesting status updates, the NRC perpetually stated that a decision on the petition would be made within three to six months."

TMIA asked the NRC to require plant operators to keep at least one armed guard at each plant entrance. The petition, which was drafted weeks before the terror attacks of 9/11, argued that the guards would serve as a physical and visual deterrent against attacks.

Since 9/11, the NRC has issued security requirements aimed at making the plants less vulnerable to attack. Changes include the addition of guard towers, truck barriers, deeper background checks and high-tech fencing. Most, if not all, plant owners post guards at their front gates.

For months after the terror attacks, Pennsylvania was among several states to assigned National Guard troops to the plants. NRC officials have denied allegations of foot dragging. Petitions such as TMIA's, which require rule changes, take a long time to complete, officials said.

The Nuclear Energy Institute, which represents plant owners and operators, opposes the petition.  It told the NRC that guards should be posted only when the level of security threat makes it prudent.

On July 29, 2005, the NRC a issued White Violation relating to another staffing deficiency at Three Mile Island where “approximately 50% of the emergency responders,” including “key responders”  were “overdue” for their annual training for “an approximate five month period. (Please refer to Thursday, July 14, 2005, for background material).

-Report by Garry Lenton of the Patriot-News

- March 30, 2005- NRC reviews Peach Bottom, plant a leader in shutdowns

Attendees seemed more in the dark last night after a 90-minute session aimed at shedding light on Peach Bottom Atomic Power Station's performance last year.

Exelon and Nuclear Regulatory Commission officials didn't exactly wow the crowd of about 40 with a slide show highlighting corporate progress, touting a 25 percent reduction in radioactive exposure to employees and diagramming federal "matrixes" and "cornerstone" safety guidelines.

One attendee asked why the commission couldn't just grade performances A to F, drop bureaucraticese and spell out problems that affect the public.

The bottom line: The NRC found that Peach Bottom improved in 2004 with two shutdowns of its Unit 2 reactor compared to three in 2003.

The shut downs placed Peach Bottom in the top three nationwide for unexpected shutdowns right behind Indian Point 2 in New York and Saint Lucie Unit 2 in Florida.

Five shutdowns in Unit 2 over two years is a lot when compared to the national average of less than one shutdown annually at the country's 103 commercial plants, said Eric Epstein of Three Mile Island Alert, a Harrisburg-based nonprofit citizens' organization.

The NRC said the shutdowns, called "scrams," were low-level safety risks but noteworthy nonetheless.

Want better procedures: Federal officials also warned the plant, operated by Exelon Corp., that its procedure in finding and reporting causes for shutdowns needs improvement. "They said our focus regarding inspections was too narrow," said Robert Braun, Exelon's site vice president at Peach Bottom. "We'll apply what they told us, which was to broaden our investigation."

Braun said that the shutdowns pose no threat to the public but only affect the company's bottom line. He further touted adherence to safety guidelines saying the plant was taking a "proactive approach." That tack, he said, would help plant workers discover problems such as the cause of a Unit 2 shutdown in July 2003.

A piece of broken fan belt that had been lost "a number of years ago" entered a cooling system and caused the shutdown. The debris wasn't found when the belt broke, but "years later it came back to haunt the plant," Braun said. "We continue to improve our existing processes," he added.

Epstein questions numbers: Epstein asked corporate and federal officials how many workers were employed at Peach Bottom, whether they had decreased in the past five years and if so, would that affect plant performance and the reduction in radiation exposure. NRC Chief of Projects Branch 4 Mohamed Shanbaky said the plant was in federal compliance with the number of employees needed for high-profile jobs such as reactor operators.

Shanbaky further said the NRC doesn't focus on the overall number of employees but rather whether federal rules are obeyed and safety regulations adhered to.

"This meeting was the NRC's assessment for 2004," said April Schlipp, Exelon spokeswoman, who added that there have been no staffing changes since the 2003 assessment. "We've been able to improve for the past two years; that's really the most relevant here."

Beth Birchall, a Lancaster County resident, sat in the back of the Peach Bottom Inn banquet room shaking her head.

"They seemed prepared," she said. "But there wasn't a lot of information."

The NRC has scheduled quarterly, team and regional inspections of the plant in 2005.

-Report by Kathy Stevens of the York Dispatch

- May 27, 2005 -Many emergency sirens would not work if power lines were down

In the event of a nuclear accident or an act of terrorism at a U.S. nuclear power station simultaneously occurring with an electrical grid failure, only 27 percent  of the nation’s 62 nuclear power emergency planning zones using public notification siren systems are prepared to fully operate their emergency sirens independent of the main power lines,”  emergency enforcement petition filed by Nuclear Information & Resource Service, Three Mile Island Alert and numerous citizens’ groups.

While the Nuclear Regulatory Commission revealed that some but not all of the sites without backup power are preparing to create battery backups, the NRC actually denied the petition, and argued that the concerned citizens should instead use a petition for rulemaking process that can take as long as two years.

Peach Bottom is  grid-dependent for sirens.

- July  2005- Peach Bottom Investigation: NRC probes shutdown at Peach Bottom

- Officials with the Nuclear Regulatory Commission will follow up

on the cause of a turbine trip that led to the automatic  shutdown of Peach Bottom Atomic Power Station's Unit 2 reactor on July 10, 2004.

At the time of the shutdown, the unit's reactor coolant system experienced a high pressure condition that caused both recirculation pumps to trip. As a result, three safety-relief valves lifted and reseated.

By Tuesday morning, the reactor had returned to 67 percent power.

In September 2004, the NRC staff, through an additional inspection, investigated the reasons behind Unit 2's four unplanned shutdowns per 7,000 critical hours, or roughly one year of operation. The unscheduled shutdowns occurred between the fourth quarter of 2002 and the fourth quarter of 2003.

On December 22, 2004, Peach Bottom Atomic Power Station's Unit 2 reactor had another emergency shutdown and was off-line for 48 hours.

- Circuit Breaker Replacement Primary Bushings Not Tested

to American National Standards Institute (ANSI) Standards

- While investigating the dedication process of a different circuit breaker

component, GE Energy-Nuclear (GE) discovered that ANSI testing had not been

accomplished for the AM breaker primary bushings used in Magne-Blast circuit

breakers. The replacement primary bushings were provided by GE Supply PSC,

Sharon Hills, Pa., and supplied to Watts Bar and Peach Bottom, units 2 and 3,

by GE as safety-related components. The NRC issued a report to inform all licensees of this issue since additional licensees may have obtained these devices through other dedicating entities.

Previously, the GE product department produced Magne-Blast circuit breakers

and switchgear, that was qualified to the appropriate ANSI C37 standards.

When the GE breaker plant operation facility was closed, GE contracted with

a vendor to manufacture primary bushings. The contractor uses a similar but

not identical insulating material, and has variations in the manufacturing

process for the bushing construction. GE dedication specifications addressed

the replacement insulation material, but not the variation in the

manufacturing process. An implicit assumption in the GE dedication

specification was that testing in compliance with the applicable ANSI

standard had been completed.

GE has determined that design tests in accordance with certain ANSI C37

Industry Standards for Switchgear were not performed prior to implementation

of bushing design changes for Parts Q0845D0123G001, and Q0845D0124G001 andG003, which have been delivered to Peach Bottom 2, 3 and Watts Bar 1 for use as replacement primary bushings in Magne-Blast circuit breakers.

For primary bushings purchased under the identified purchase orders and

placed in inventory, GE recommended that the primary bushings in inventory

not be installed until after successful completion of the ANSI standards testing.

For primary bushings purchased under the identified purchase orders and

installed in Magne-Blast circuit breakers, GE recommended that no corrective

or preventive action be taken, pending completion of the ANSI standards testing.

- From reports by York Daily Record and NRC documents

- July 21, 2005 - Inspection finds only 'Green' problems

An inspection of the Peach Bottom Atomic Power Station resulted in two findings of "very low safety significance" that were categorized as Green by the NRC. Neither finding was cited, according to the report.

A report on the inspection by the Nuclear Regulatory Commission stated that Peach Bottom staff identified "inadequate procurement of quality services for the commercial grade dedication of the Unit 3 high pressure coolant injection(HPCI) electronic flow controller." The report explained the internal power supply was not properly identified for replacement to "preclude any age-related degradation" and failed while installed in the Unit 3 HPCI.

The report said this failure affects the ability to ensure "the availability, reliability and capability of system that respond to an initiating event to prevent undesirable circumstances." A single train system was unavailable for less than three days because of this loss of safety function, the report said.

Another finding showed that procedure instructions prepared but not in a timely manner, upon discovery of an inoperable  component and leakage of a component boundary for Unit 2. The leak was repaired and Unit 2 returned to service, the report said, explaining why, though the finding was considered "greater than minor" that there was no citation.

-Report by Marlene Lang

Aug. 30, 2005 -Peach Bottom's mid-cycle performance review receives a 'White' rating for three shutdowns in 12 quarters

The Peach Bottom Atomic Power Station Unit 2 had what the NRC terms "three scrams" with a "loss of normal heat removal" all within 12 calendar quarters, the plant earned itself an unusual White Performance Indicator (PI).

A SCRAM is an industry acronym representing a nuclear reactor shutdown (Skived Coke Rod Adversive Motion).

All of the other findings by inspectors were classified as Green, and considered of "very low safety significance."

-Report by Marlene Lang

- Sept. 12, 2005 - NRC inspectors: No findings of significance at Peach Bottom

The Nuclear Regulatory Commission released a report on its most recent inspcection of the Peach Bottom Atomic Power Station, saying no findings of significance were identified, but adding that minor problems were found.

The report went on to explain that "causal evaluations for equipment issues and events reasonably identified the causes of the problem and developed appropriately corrective actions." The report added, "However, for some of the issues affecting human performance, the evaluations were not of sufficient depth to identify the base root cause; therefore, the corrective actions did not prevent further human performance errors of a similar nature."

In two cases, read the report, "operability determinations did not consider all the applicable information to support the final conclusion that the equipment was operable."

Corrective actions were typically implemented in a timely manner, the inspectors said, but added that they found in one case, "corrective actions were not adequate to correct the problem, and did not prevent reoccurrence."

-Report by Marlene Lang

- Sept. 13, 2005 -Peach Bottom 2 nuke exits outage

- Exelon Corp.'s  1,112-megawatt Unit 2 reactor at the Peach Bottom

nuclear power station in Pennsylvania exited an outage and ramped

up to 43 percent of capacity by early Tuesday, the U.S. Nuclear

Regulatory Commission said in a report.

- Report by Reuters

Sept. 19, 2005 -In a failure to follow procedures, plant operators entered the Unit 3 reactor's drywell after a reactor shutdown but did not, before entering, collect and analyze a radiation sample for airborne particulate and iodine, as required by code.

The failure could have resulted in worker radiation exposure at unsafe dose levels, said a Nuclear Regulatory Commission report made in January, 2006.

Because the two individuals who entered did not sustain any significant dose, no citation was made and the finding was labeled Green.

- Sept. 30, 2005 -Fire barrier systems inadequate in real fires, says NIRS

At a public meeting, Nuclear Regulatory Commission staff "announced their recommendation to the Commission to drop a proposed rule making that would substitute controversial "manual actions" for federally required nuclear power station fire protection requirements on electrical cablling (physical fires, minimal cable separation with automated detection and suppression) vital to shutting down the reactor in the event of a significant fire," according to an industry newsletter.

According to Nuclear Information & Resource Service (NIRS), "Since 1992, NIRS has identified widespread nuclear industry violations where fire barrier systems, .... have dramatically failed standardized industry fire tests and would likely fail to protect reactor safety systems in the event of a real fire."

The NRC subsequently declared the fire barriers "inoperable" for protecting electrical power circuits, control and instrumentation cables used in the event of fire to remotely operate reactor shutdown.

As a result, the NIRS explained in the Oct. 14, 2005 issue of Nuclear Monitor, "the majority of the U.S. nuclear power industry was found to be in violation of safety standards as prescribed under current Code of Federal Regulation."

The report went on to say that "the federal agency (NRC) failed to take effective enforcement action and require that operators become compliant with the current fire protection law by installing qualified fire barriers or maintaining minimal separation requirements between electrical circuits for reactor safety-related equipment.

- Oct. 31, 2005 -NRC announces inspection

The NRC informed Exelon Nuclear that  it would perform a triennial fire protection baseline inspection in January and February of 2006. A letter stated the NRC would make an information gathering visit the week of Jan. 9 and would perform the onsite inspection the weeks of Jan. 23-28 and Feb. 6-10.

- Nov. 1, 2005- Inspectors find three federal code violations, issue no citations

An airborne radiation sampler was not sampling correctly, NRC inspectors discovered during an integrated inspection of the Peach Bottom Atomic Power Station.

The inspection, which was completed Sept. 30, turned up three issues, none of which resulted in a citation.

The radioiodine and particulate sampler is required to be in one of the highest annual average ground level D/Q areas. The report also said that Exelon had failed to conduct vegetation or milk sampling of highest calculated annal average ground level D/Q at the nearest offsite garden. The report did not explain what "D/Q" was an abbreviation for.

The report said the failure could affect "protection of public health and safety from exposure to radioactive materials released into the public domain." However, the finding was considered of "very low safety significance" because "calculations of public dose commitments did not identify andy significant public dose or environmental impacts."

NRC inspectors also found that emergency workers required to use respiratory equipment had not maintained their qualifications. The violation affects readiness, the report stated, which in turn could put public health and safety at risk in a radiological emergency. The matter was deemed of "very low safety significance." Owner Exelon was not cited.

Exelon was not cited, either, after its Peach Bottom staff failed to "implement established procedures adherence standards during recovery from an aborted routine test." Operators did not perform the appropriate portions of the restoration section, did not initiate a temporary procedure change, and did not seek technical support after receiving an unexpected test result, according to the report. The error contributed to a reactor trip, but did not result in a citation because the error did not increase the likelihood of equipment or functions being unavailable, the NRC report stated.

-Report by Marlene Lang

- Jan. 22, 2006- Fire watch technician pleads guilty to falsifying records

A contracted employee at the Peach Bottom Atomic Power Station pleaded guilty Jan. 9 to the falsification of records used to safely operate the dual-reactor nuclear power plant. Between Jan. 17, 2005, and March 20, 2005, Tracy David, formerly of Bartlett Service Inc., failed to conduct hourly fire watch inspections in multiple sections of the plant including the emergency diesel generator room and the cable spreading room. Contacted by telephone, David - a resident of Quarryville, Pa., according to court documents - declined to be interviewed for this story. Based in Plymouth, Mass., Bartlett Services is a subcontractor for the Peach Bottom Atomic Power Station. On 199 occasions, David claimed that she had completed her rounds of fire watch inspections while on duty at the plant, said Neil Sheehan, spokesman for the U.S. Nuclear Regulatory

Commission. Last year, both the NRC and plant officials ran independent investigations that uncovered evidence that showed that David had falsified her fire watch inspections and had not completed her rounds.When interviewed by representatives of the NRC's Office of Investigations, David commented that one reason for her accused

offense was that she had been disgruntled after being passed over for a promotion, Sheehan said."There were a significant number of fire watches that were

missed," he said. "But (the plant) still had fire suppression systems in place."Regardless of the seriousness of the charges, the commission found that the safety significance was low since no fires werereported and each room on David's route was equipped with

automatic fire-detection systems, Sheehan said. A fire watch technician walks a predetermined route, checking sections of the plant for smoke or other signs of fire, said

Paul Gunter, director of the reactor watchdog project for the Nuclear Information and Resource Service. The technician keeps=records of hourly checks to ensure that each room has beenmonitored at a particular time."The job is pretty monotonous," said April Schilpp, a spokeswoman for the plant. Gunter said his organization has tracked fire protection violations at nuclear power plants since the early 1990s. For many years, Gunter's group has argued for improved fire barriers and other systems rather than rely on fire watches."(Plants) should put in adequate fire protection features," he said. "You put humans into the picture, there will be an error. Especially with roving fire watches."

The manual fire watch checks serve as a compensatory measure as ordered by the NRC. The commission requires that fire watches be conducted for any room inside a plant that has its fire detectors on automatic but its fire suppression system on manual. At times, a plant may switch its fire suppression equipment to manual if the system proves too sensitive, Sheehan said. Should a fire watch patrol worker spot signs of smoke, the

worker would immediately notify the on-site firefighting brigade, he said."It is a very important function," Sheehan said. Along her route, David's duty's took her to the plant's cable spreading room and to the emergency diesel generator room - the

site of a small June 2003 fire.

- Peach Bottom Atomic Power Station is equipped with four

emergency diesel generators that kick on when the plant loses

power.

- The generators serve as a source of backup energy. They power

the plant's vital equipment including systems used to safely

shut down the power station, Sheehan said.

- In June 2003, NRC inspectors found that plant technicians had

not adequately tightened the engine top cover flange joint bolts

of an emergency diesel generator during a maintenance procedure.

- As a result, lube oil leaked from the joint and caused a small

fire on the exhaust manifold during a test.

- While no fires occurred during David's shifts, an internal

investigation carried out by Peach Bottom Atomic Power Station

officials did raise eyebrows concerning David's actions while on

the job.

- In February, while on duty, David's personal dosimeter sounded

when it should not have gone off, Schilpp said. Typically worn

around the neck, a dosimeter is a pager-sized piece of equipment

that measures and detects radiation.

- As part of the plant procedure, when a worker's dosimeter

sounds, that person must leave the room and locate a plant

technician, Schilpp said.

- A quick check found that David had come from an area of the

plant that was not part of her route, Schilpp said.

- "She was not supposed to anywhere near that area," Schilpp

said. "At that point, (the plant) started to question other

things."

- As part of the investigation, plant officials checked previous

dosimeter readings and found that, in some cases, David's scans

did not match what they should have been for her predetermined

route.

- Plant investigators tracked David by her badge, which is

needed as a key to enter specific areas of the site.

- "The evidence was overwhelming that things were not going

right," Schilpp said. "We saw a pattern emerge."

- At the onset of its own investigation, the plant alerted the

NRC to the situation, she said.

- "We self-identified the problem," Schilpp said. "We want

people to be doing the things we ask them to do and to fulfill

the obligations of our license."

- Site officials confronted David with their evidence and

conducted an interview to make sure the plant had not been

deficient in explaining to the contracted employee what her job

had entailed.

"She told us that she fully understood the job," Schilpp said,

adding, "We don't want this to happen again."

- Peach Bottom notified Bartlett Services that David had not

been doing her job as assigned and had falsified fire watch

records.

- Bartlett Services removed David from her fire watch position

at Peach Bottom Atomic Power Station in late March. On April 15,

the NRC opened its own investigation.

- Since the commission is not a legal or judicial agency, the

NRC notified the U.S. Department of Justice of its

investigation. The Department of Justice, in turn, accepted the

case for potential action.

- "If we have findings of a criminal or deliberate nature,"

Sheehan said, "we refer those to the (U.S. Department of

Justice)."

- At the guilty plea proceedings held earlier this month, David

acknowledged that she had falsified her fire watch records, said

Martin Carlson, the assistant U.S. attorney assigned to the case.

A sentencing date for David has not yet been set.

-Report by Sean Adkins of the York Daily Record/Sunday News

Jan. 25, 2006- An integrated inspection of Exelon Nuclear's Peach Bottom Atomic Power Plant documented two violations, neither of which resulted in citation of Exelon by the Nuclear Regulatory Commission.

In a failure to follow procedures, plant operators on Sept. 19, 2005, entered the Unit 3 reactor's drywell after a reactor shutdown but did not, before entering, collect and analyze a radiation sample for airborne particulate and iodine, as required by code.

The failure could have resulted in worker radiation exposure at unsafe dose levels, the report said.

Because the two individuals who entered did not sustain any significant dose, no citation was made and the finding was labeled Green.

Nor was a citation made when NRC inspectors discovered that following a valve replacement, high pressure service water (HPWS) was not adequately tested. The report stated that "The post-maintenance test did not account for the known degraded condition of the 3B residual heat removal heat exchanger HPSW outlet throttle valve. Improper test control on two occasions did not identify that high pressure service water flow through the section was below the established "design basis" flow.

The finding was categorized as Green, the report explained, because it did not result in a loss of function.

-Report by Marlene Lang

- Feb. 10, 2006 - Fire inspection finds nothing significant

A fire protection inspection of the Peach Bottom Atomic Power Station resulted in "no significant findings" by federal inspectors.

A report on the inspection, from the Nuclear Regulatory Commission, dated March 9, 2006, stated that the purpose of the triennial fire protection inspection was to assess whether Peach Bottom owner Exelon had implemented and adequate fire protection program and that "post-fire safe shutdown capabilities have been established and are being properly maintained."

-Report by Marlene Lang

- Feb. 19, 2006- Peach Bottom reactor operating after shut down

The operators of Three Mile Island, Peach Bottom and Limerick nuclear power plants are checking their systems for leaks of water laced with tritium, a radioactive isotope linked to cancer.

Chicago-based Exelon Energy Co., which owns the plants, ordered the inspections after water contaminated with tritium was found in the groundwater or in test wells at three of its plants in Illinois. Exelon owns 10 nuclear plants.

The company ordered each plant to conduct inspections of systems that carry tritium-laced water. The inspections will include pipes, pumps, valves, tanks and other equipment, said Ralph DeSantis, a spokesman for AmerGen Energy, the operator of TMI and a subsidiary of Exelon.

Tritium, a radioactive isotope of hydrogen, is a byproduct of the nuclear reaction. In large doses, it has been linked to cancer.

"Our purpose is to ensure that we have a full understanding of the health of our systems that handle tritium and that we have satisfied ourselves ... that our equipment has a high degree of integrity," said Charles Pardee, Exelon's nuclear chief operating officer.

TMI officials have been monitoring tritium since shortly after the 1979 accident that destroyed the Unit 2 reactor. About a dozen monitoring wells are checked at TMI quarterly, DeSantis said.

Higher-than-usual tritium levels were found in a test well at TMI last fall, said David Allard, the director of the state Department of Environmental Protection's Radiation Control Program. The amounts never exceeded 19,000 picocuries per liter of water. The U.S. Environmental Protection Agency allows up to 20,000 picocuries per liter in drinking water. There is no standard for groundwater.

The leak was traced to a sump pump and corrected, Allard said.

Tritium-laced water is routinely released into the Susquehanna River by TMI, where it is diluted.

The DEP monitors the river at Steelton and Columbia. "I'd be very surprised if we ever saw any tritium," Allard said.

Eric Epstein, the chairman of the watchdog group Three Mile Island Alert, called on Exelon to be more aggressive with its well testing.

The EPA describes tritium as one of the least dangerous radioactive substances because it emits weak radiation and usually leaves the body within a month.

-Report by Garry Lenton of the Patriot-News

- Feb. 27, 2006 -Fire cause power reduction, 'no threat'

A electrical fired occurred at Peach Bottom's Unit 3 transformer, forcing the plant to reduce power to 50 percent.

Exelon and government officials said the fire posed no threat to the public, as it happened in a non-nuclear area of the plant, shortly after 9 a.m. It was extinguished by 10:32 a.m., officials said.

The fire was traced to a transformer cabinet in the turbine building of the Unit 3 reactor, said April Schlipp, spokeswoman for the plant's owner, Exelon Nuclear.

-Report by Garry Lenton

- Feb. 28, 2006 - NRC examing TMI security

The U.S. Nuclear Regulatory Commission plans to investigate the management of the security force at Three Mile Island, focusing on fitness-for-duty issues such as fatigue and sleeping on the job.

The probe, announced in a certified letter delivered to a Patriot-News reporter, was prompted by a story published Jan. 29.

The story reported on a memo in which John Young, head of the Wackenhut security, scolded security supervisors for failing to note that veteran officers were telling new hires safe places to sleep undetected while on duty. Wackenhut is a private security firm hired by plant owner Exelon Nuclear to guard the nuclear station.

The memo also said officers were telling new hires ways to short-cut patrol duties.

Of additional concern to the NRC were reports that security officers were being allowed to work excessive hours. The newspaper documented one person who worked more than 150 hours during a 14-day period, and averaged more than 54 hours a week for more than 10 months.

Since March 2004, AmerGen Energy, the operator of TMI, investigated and disciplined five workers for "inattentiveness to duty." The phrase is used by the industry and regulators to cover an array of conditions, including sleeping. Three of those workers were security officers.

Guards, speaking on the condition of anonymity, said fatigue from long hours and boredom were to blame for the inattentiveness.

Guards work 12-hour shifts at TMI. Federal regulations limit those hours to 16 out of 24; 26 hours out of 48; and 72 out of seven days.

The agency said it will not announce the findings of the probe.

"Due to the nature of the security-related issues ... we are not providing you with further information on this matter," wrote David J. Vito, senior allegation coordinator for the NRC.

-Report by Garry Lenton of the Patriot-News

- March 1, 2006- Drop-in inspections planned by state

Prompted by reports of sleeping or inattentive employees at Three Mile Island, the state said it will conduct surprise inspections at least twice a month at Pennsylvania's five nuclear power plants.

The first round of inspections last month found no instances of inattentiveness on the part of control roomoperators or plant security, Gov. Ed Rendell said yesterday.

The state Department of Environmental Protection will continue the inspections through the end of the year. Then the DEP will decide whether to continue the practice, said Ronald Ruman, a department spokesman.

The inspections came shortly after The Patriot-News reported on five cases of inattentiveness at TMI that occurred since March 2004.

Report by Garry Lenton of the Patriot-News

- March 2, 2006- NRC notes three shutdowns of Unit 2

Peach Bottom's annual assessment of it nuclear reactors noted that the Atomic Power Station's Unit 2 reactor was shut down three times in 12 quarters, "with a loss of normal heat removal," a rate which resulted in a "White" level performance indicator. White is the second least significant, just above Green.

-Report by Marlene Lang

- March 15, 2006 -NRC responds: Incidents unrelated

The NRC's Senior Allegation Coordinator responded to TMIA's Eric Epstein, in a letter, saying that two incidents of workers falsifying records at the Peach Bottom plant were unrelated and did not represent a pervasive problem.

One incident involved a fire-watch report in January 2006. Another, in October 2001, involved falsification of maintenance tests on sirens.

-Report by Marlene Lang

May 3, 2006 - Nuclear Regulatory Commission inspectors found Peach Bottom was not adequately testing it E-2 emergency diesel generator (EDG) air coolant auxiliary pump following shaft packing replacement, according to a report on an inspection completed March 31, 2006.

A post-maintenance test did not account for the higher pressure that occurs in the EDG cooling subsystem when the EDG is operating and the cooling system is pressurized by the attached cooling pump, the NRC report explained. Ten gallons of water leaked on the  floor in the area of the EDG, as a result, and the leak occurred over a 22-hour period on Dec. 27 and 28, 2005.

The report further stated that personnel had "an inadequate understanding of the air coolant auxiliary pump design and the pump's interrelation with the EDG operation," though the information was available to the testers.

The finding was label Green and owner Exelon was not cited, though a plan was made to correct the problem, the report said.

Inspectors also reviewed an event that happen on Jan. 1, 2006, in which a Unit 2 reactor control rod drive (CRD) system flow transmitter failed by "drifting low." This resulted in an increased control rod drive flow as the flow control valve open in an attempt to compensate for the low flow in the CRD system and according to the report, the condition was not immediately identified. Core thermal power increased and operators reduced power while the situation was evaluated. It turned out that the system was not at in overpower condition.

Also noted in the report, on Feb 13, 2006, operators forgot to complete required technical specification tests after a slow start of an emergency diesel generator. They remember three hours later to do the tests, the report stated.

None of the incidents resulted in citations, as they were considered of low safety significance.

-Report by Marlene Lang

May 12, 2006 - The NRC evaluated Emergency Preparedness exercises held April 25 at Peach Bottom's Unit 2 and Unit 3, reporting no findings of significance.

- May 17, 2006- After employee falsified records, plant stays in compliance, with firing

- The federal Nuclear Regulatory Commission gave its lowest form of

enforcement notice to the nuclear power plant in Peach Bottom Township

after an investigation into falsified plant records.

Peach Bottom Atomic Power Station sidestepped a more severe infraction

from the regulatory agency by identifying and immediately acting on

the violation by a contracted employee, the federal commission said in

a letter dated May 12.

As part of a backup verification to its fire safety system, Exelon Corp. contracts with Bartlett Service of Massachusetts to enter certain rooms and verify there is no fire or risk of a fire.

Between January and March of 2005, Exelon determined an employee of

- Bartlett – whom the commission did not name – falsified records on

the fire watch logs on almost 200 occasions.

- When Exelon realized what had happened, the employee was fired, and

the company started its own investigation, along with notifying the

proper authorities of the violation.

- In the letter to Exelon, the commission said it considered a more

severe infraction, but settled on a "non-cited violation." As a

result, the power plant must take corrective action to improve the

fire watch performance and prevent the violation from happening again

– which the commission noted Exelon had already done a year prior.

"You restored compliance immediately after identification of the violation by terminating the employee," the commission said in the letter, "and by conducting a prompt investigation to review the access records for other contractor fire watch staff that concluded that the individual's action was an isolated case."

- The violation was classified at Severity Level IV, the lowest severity

level. In comparison, commission spokeswoman Diane Screnci said a

- Severity Level III violation would have included the consideration of

a fine.

- Exelon agreed with the level of severity set by the commission, said

April Schilpp, a spokeswoman for the Peach Bottom power plant.

-Report by Charles Schillinger of the York Dispatch

- June 1, 2006- Inspection turns up one test issue

An NRC inspection completed on April 21, 2006 turned up one low-significance finding, according to a report released June 1.

Inspectors reported that Peach Bottom operators failed to ensure that test procedures for the high pressure coolant injection (HPCI) and the reactor core isolation cooling (RCIC) pump had acceptance criteria incorporating limits from design documents. Failing to stay within the limits for which the pump was designed could degrade the pump to a lower limit could interfere with proper flow and discharge pressure. The finding was not cited and a correction plan was made, the report stated.

-Report by Marlene Lang

June 30, 2006 - The NRC completed an integrated inspection of the Peach Bottom Atomic Power Station with four findings, all rated "Green," and all not cited.

One finding by inspectors involved barrier integrity, according to a report on the inspection, dated July 26, 2006.

Exelon was to compare task performance between its plants at Limerick and Peach Bottom, according to company procedures established in 1991, the report stated. Inspectors found that three out of five job performance measures for Limerick Senior Reactor Operators who handled fuel differed significantly in the way they were performed. The NRC report said the differences should have been explored, but were not, and that the failure could have affected physical design barriers that protects the public from radionuclide releases. The finding was not cited.

In another Green finding, personnel failed to properly implement procedures for a high pressure coolant injection (HPCI) turbine exhaust drain piping.

This failure, the report explained, preventd an HPCI containment isolation valve closure on April 5, 2006. The matter was considered of very low safety significance because it did not represent an actual open pathway in the physical integrity of the barrier.

There was also a finding that affected emergency preparedness. Inspectors found a ready-for-use self-contained emergency apparatus in the main control room which had a partially separated regulator air diffuser. The finding was categorized as Green.

In a violation of NRC requirements that one residual heat removal (RHR) shutdown cooling system (for high water level) be operable and in operation during a shutdown, and this was not the case in instances in September 2002 and 2003. No citation was made as there were no actual safety consequences caused by the failure.

-Report by Marlene Lang

- July 24, 2006 - NRC responds to fire watch concerns: There is no chronic problem

A Nuclear Regulatory Commission official responded to Eric Epstein's June 12, 2006 letter, in which Epstein ask whether the NRC believed there were a chronic problem at Peach Bottom regarding missed fire watches.

The NRC stated they did a historic review of missed fire watches at the plant and that no chronic problem was found.

Epstein was also told that there was no adverse issue with documentation falsification, after an inquiry.

Epstein asked about a matrix being used to reach these conclusions and the NRC stated it did not use a "matrix" but instead made inspections and reviews.

-Report by Marlene Lang

Aug. 16, 2006- 'Unusual Event' Declared, Terminated at Peach Bottom Plant in York County

Exelon Nuclear’s Peach Bottom Atomic Power Station’s fire brigade extinguished a small fire onsite yesterday after a backup emergency diesel generator’s exhaust gasket on the roof of the diesel generator building unexpectedly caught fire.

The fire occurred during routine testing of one of the station’s four diesel generators. The fire prompted the declaration of an Unusual Event at 6:14 p.m. Tuesday, in accordance with station procedures, due to a fire in the Protected Area that was not extinguished within 15 minutes. The fire was extinguished at 6:35, and the Event was terminated at 8:40 p.m. No offsite fire responders were needed to extinguish the fire.

There was no threat to the safe operation of the plant, and there was no danger to station personnel.

An Unusual Event is the lowest of four emergency classifications established by the U.S. Nuclear Regulatory Commission. There was no danger to the public during the event and no special action by the public was needed.

Exelon Nuclear notified all appropriate federal, state and local emergency response officials of the Unusual Event.

- Oct. 11, 2006 -Reactor back in service

A nuclear power plant reactor in southern York County returned to service yesterday morning after a cracked pipe in the cooling system forced owner Exelon Nuclear to shut the reactor down Saturday night.

The shutdown was the second at the Peach Bottom Nuclear Station in 15 months and the third since 2003.

The reactor, which had been off line for three weeks for refueling and maintenance, was only two hours into its restart when an equipment operator noticed a leak in a pipe used to test the cooling system, said April Schilpp, spokeswoman for the plant.

-Report by Garry Lenton of the Patriot-News

- Oct. 20, 2006 - Peach Bottom among nuclear power plants included in study

The Peach Bottom nuclear power plant in Pennsylvania and Seabrook Station in New Hampshire has been chosen as one of six nuclear power plants nationwide to be part of a study of the consequences of an accident that would release radioactivity into the atmosphere.

The other nuclear plants being reviewed are Diablo Canyon in California; Duane Arnold in Iowa; Fermi in Michigan; and Salem in New Jersey. The study is expected to take three years.

"The sites were picked based on the demographics of the surrounding communities and the type of containment used," said Scott Brunnell of the Nuclear Regulatory Commission.

The study will bring together information about how accidents could occur within containment buildings; how containment could be breached; how radioactive plumes could travel; and how effective emergency planning would be, Brunnell said.

Ultimately, the criteria developed as a result of this study would be applied to all U.S. nuclear power plants, Brunnell said.

Seabrook Station spokesman Alan Griffith said that all nuclear plants would eventually be reviewed. He said this is an effort on the part of the NRC to update its methodology.

"It will be beneficial to the community because the NRC will be taking a look at emergency planning," Griffith said. "Ultimately, it will be good for all of us."

-Report by the Portsmouth Herald

- Feb. 5. 2007- Operators compensate for low system settings

An integrated inspection by the NRC found Peach Bottom workers failed to follow procedure for equipment evaluations involving pressure pulsations going into standby liquid control (SLC) systems in which relief valves were degraded.

According to a report, on Nov. 21, 2006, engineering personnel documented the incorrect setting of SLC pump relief valves. During the rebuild of Peach Bottom's Unit 3 on Nov. 1, 2004, an SLC pump discharge relief valve was incorrectly adjusted from its design setpoint. There were similar setting questions about Unit 2 and engineers determined that Units 2 and 3 SLC systems were degraded and set low, but still operable, with  "two compensatory actions" to maintain pressure. The report noted the relief valves were scheduled to be replaced during each unit's next refueling outage.

The finding was considered of very low safety significance and was not cited.

-Report by Marlene Lang

- Feb. 28, 2007- Power plant fire not a threat, officials say

An electrical fire at the Peach Bottom nuclear station in southern York County yesterday posed no threat to the plant's operating nuclear reactors, according to company and government officials.

The fire, discovered shortly after 9 a.m. in a non-nuclear area, was extinguished by 10:32 a.m. and there were no injuries, officials said.

The fire was traced to a transformer cabinet in the turbine building of the Unit 3 reactor, said April Schilpp, spokeswoman for the plant's owner, Exelon Nuclear. As a precaution, officials shut down the turbine and cut power to 50 percent.

Company officials were assessing the damages, but they were expected to be minor.

"It should not prevent the plant from operating normally," Schilpp said.

U.S. Nuclear Regulatory Commission spokeswoman Diane Screnci said the plant was stable and that its inspectors were in the plant control room monitoring the situation.

The fire is the ninth at Peach Bottom since 1986, and the second in the Unit-3 turbine buildings, according to a chronology put together by the watchdog group Three Mile Island Alert using NRC documents.

The most recent was a small fire in an emergency backup diesel generator in August, 2004.

"Fires at nuclear power plants are never a welcome development," said TMIA Chairman Eric Epstein. "Older plants with aging parts, like Peach Bottom, require heightened vigilance. The root cause needs to be identified and defeated."

-Report by Garry Lenton of the Patriot-News

- March 17, 2007- Fire was electrical

The Pennsylvania Department of Natural Resources reported that it was a breaker that caught on fire at the Peach Bottom plant in February. A spokesman said the fire was electrical in nature.

"They replaced the breaker and verified proper connections and amperages to prevent a recurrence. I have not yet seen the utility's root cause evaluation, but Dennis Dyckman of my staff is following up on this with the plant," according to Rich Janati, of the DEP.

March 20, 2007- A former security manager for Wackenhut Coporation reportedly sent a letter to the Project on Government Oversight, who passed it on the the Office of the Inspector General on March 27. The writer of the letter claimed that Peach Bottom security officers were fatigued from working excessive overtime or 12-hour shifts and would cover for each other so they could take naps of 10 minutes or more during shifts. According to an NRC memo released Aug. 22, 2008, the letter also indicate the past efforts by the NRC to identify personnel sleeping on duty had failed, and alleged that NRC and Exelon were aware that officers were sleeping while on duty, and said security officers feared retaliation for raising safety concerns.

The memo stated the letter was provided to the Nuclear Regulatory Commission resident inspector at Peach Bottom in March 2007, and that at that time the concerns it relayed were evaluated under the NRC allegation program by the NRC's Region I office, which oversees Peach Bottom.

In August 2007, Region I concluded the concerns were not substantiated and the allegation filed was closed, according to an NRC document.

-Report by Marlene Lang

2007

March 2007- John Jasinski sends the Nuclear Regulatory Commission a letter alleging guards are sleeping throughout the nuclear plant in York County, Pa. The NRC refers the concern to plant owner Exelon and security provider Wackenhut.

- March 13, 2007- NRC: 2002 miscue accidental

In 2002, a plant security officer falsified fire watch logs at Peach   Bottom Atomic Power Station.

A contracted security officer at Peach Bottom Atomic Power Station - who logged a fire watch he didn't actually perform - did not willfully falsify fire watch records, according to a U.S. Nuclear Regulatory Commission investigation.

In April 2002, a Wackenhut contract security officer did not conduct a required fire watch but indicated on a log sheet that the action had been completed, according to NRC Office of Investigations records.

While investigating an unrelated matter in July 2006, commission investigators learned about the 2002 missed fire watch, said Neil Sheehan, a commission spokesman.

Investigators discovered that the officer believed his missed fire watch would be conducted by another officer during a scheduled tour of that same area. However, the second officer was assigned to cover the area once every four hours and not every hour as required to cover fire watches.

- April 11, 2007 -Security guards to receive back wages

The Miami-based company that employs guards at Peach Bottom Atomic Power Station has agreed to pay $129,953 in back wages to 157 workers at the nuclear-powered plant.

A U.S. Department of Labor's Wages and Hour Division investigation found that Wackenhut Corp. paid guards their regular rates of pay regardless of how many hours they worked.

A federal act states that employees must be paid time and a half should they work more than 40 hours per week.

In the case of Wackenhut Corp., the company required security guards to arm themselves prior to the start of their shift, said Leni Uddyback-Forston, a spokeswoman for the U.S. Department of Labor. "The arming-up process could take five to 15 minutes per employee each day" she said. "They were not being compensated for that time."

Also, regular changes to Wackenhut's work schedule resulted in some guards being paid for four hours at their regular rate instead of overtime pay, Uddyback-Forston said.

Wackenhut officers guard both Three Mile Island in Dauphin County and Peach Bottom Atomic Power Station.

A representative from Wackenhut Nuclear Services said he could not comment on the reimbursement of the Peach Bottom Atomic Power Station guards.

Wackenhut has paid more than 90 percent of the back wages owed, Uddyback-Forston said.

The company is in the process of reimbursing the remaining 26 of 157 guards affected, she said.

-Report by Sean Adkins of the York Dispatch

- April 19, 2007- Plant owners request 'reduction' to code

Exelon Generation Company and AmerGen Energy Company asked the Nuclear Regulatory Commision for approval of a change to the required Quality Assurance Topical Report, required under federal code. The companies explained the requested changes to the fire protection program represents a "reduction in committment."

The NRC said it would need more information to complete a review of the request. Federal code requires the NRC Safety Review Committee to inspect and audit the fire protection program, and the NRC asked the companies to describe how the topical report in question "establishes a requirement for the inspection and audit of the fire protection program."

Twelve nuclear power plants would be included in the requested code change.

-Marlene Lang

- April 26, 2007- Work hours to be limited for some nuclear plant workers

Security workers and others in critical jobs at the nation's nuclear plants will no longer be allowed to log excessive overtime hours under new rules approved by the U.S. Nuclear Regulatory Commission.

The change in the NRC's "fitness for duty" requirements is meant to reduce fatigue among plant employees and improve safety and security.

Exelon Nuclear, owner of Three Mile Island, Peach Bottom and Limerick nuclear stations in Pennsylvania, and seven other plants nationwide, expects to increase security staffing to reduce overtime.

"Any area where you have 24/7 coverage is most likely to be impacted," said Craig Nesbit, a spokesman for the company.

The regulations, which should go into effect this year, end a policy that allowed plant operators to meet work-hour limits by averaging the hours of dozens of employees. The process allowed some employees to log hundreds of hours of overtime a month. The new rule bases hourly limits on individuals.

The work-hour limits apply to security, maintenance and operations staffers, such as control room operators.

The rule is common sense, said Dave Lochbaum, a nuclear safety expert with the Union of Concerned Scientists, a Washington, D.C.-based watchdog group.

"Groups don't get tired. People do," he said.

David Desaulniers, an NRC staffer who helped shepherd the rule change through a seven-year administrative review, said the revision will improve plant safety.

"I think that what the commission has approved will be a substantial step forward in addressing worker fatigue issues in the future," said Desaulniers, senior human factors analyst for the agency.

The shortcomings of group averaging were evident at TMI, where some security officers employed by Wackenhut Nuclear Services logged 72-hour weeks for six weeks straight last year.

In 2005, TMI officials cited three security workers for being inattentive or sleeping on the job. Each incident occurred during the night shift. Security officers contacted by The Patriot-News at the time said the incidents were not surprising given the overtime officers were being compelled to work.

The NRC rule, which must undergo review by the federal Office of Management and budget before it goes into effect, also:

• Increases the minimum break between shifts from eight hours to 10.

• Establishes training requirements for fatigue management.

• Limits the reasons plant operators may waive the hourly limits.

• Revises drug- and alcohol-testing requirements.

A veteran security officer at TMI employed by Wackenhut welcomed the changes. "It will definitely keep things from getting really bad again like they were in '02 and '03," said the officer, who spoke on the condition that he not be identified.

Another officer, also requesting anonymity, said the change would significantly reduce fatigue. But he remained skeptical of how much leeway employers would have to waive the rules under special circumstances.

Though the NRC establishes the regulations, it does not require plants to obtain agency approval before authorizing a worker to go over the limit.

Eric Epstein, chairman of the Harrisburg-based watchdog group Three Mile Island Alert, had similar concerns. "I believe the standards are contingent upon voluntary compliance," he said. "I see nothing that suggests there will be more aggressive oversight of a new fitness-for-duty program."

-Report by Garry Lenton of the Patriot-News

- April 30, 2007- NRC calls fudged fire checks "minor"

The NRC wrote Peach Bottom to report on an investigation of Jan. 19, 2006 incident in which an employer deliberately did not make the fire protection surveillance rounds required, and falsified reports to say the checks were made.

The NRC told Peach Bottom owner Exelon, "Because you are responsible for the actions of your employees, and because the violation was willful, the violation was evaluated under the NRC ... process. .... The NRC considered that the violation, absent willfullness, would be of minor safety significance because the fire safety equipment was maintained in a functional condition."

The report went on to say: "However, the NRC escalated the severity level of Severity Level IV because the violation was a deliberate act."

-Report by Marlene Lang

- May 3, 2007 -NRC alerts power plants of fires

Operators told to review fire protection plans

The Nuclear Regulatory Commission informed power plant operators of two fire incidents, and their causes.

On Aug. 15, 2006, at the Peach Bottom Atomic Power Station, combustible, improperly installed roofing materials on an emergency diesel generator caught fire where it came into contact with a steel penetration sleeve which the generator's exhaust passes through. According to a letter from the NRC to nuclear plant operators, the fire smoldered for about 35 minutes, from the time it was fire identified until it was put out by the plant's in-house fire brigade.

Peach Bottom found that some of the roofing materials were improperly installed back in 1997-98, and were abutting the steel sleeve. The report explained that during an extended run of the emergency generator the steel sleeve "heated to the point that it caused the adjacent roofing materials to ignite." The exhaust stack operates at about 900 degrees Fahrenheit, but asphalt roofing paper burns at about 400 degrees.

Another fire occurred Aug. 18, 2006 at the Beaver Valley Power Station, Unit 1 reactor, during ventilation duct installation, through a concrete wall which served as a contamination barrier. A worker had stuffed combustible cotton rags around the venting, and sealed it with duct tape. When welding began, heat transfer through a metal sleeve box ignited the duct tape and rags.

According to the NRC report, the burning rags and melting plastic fell through the concrete wall opening into the cable vault. Drops of hot burning plastic fell into conduit-protected cables.

There was no continuous fire watch on the cable vault side of the fire barrier, but smoke from the burning plastic activated a smoke detector. The fire burned about six minutes, and was put out by hand, by a worker, the report said.

Nuclear power plants were told to review their fire protection plans with this information in mind. No specific requirements were made, or specific actions required of plants.

- May 8, 2007 - Worker faking records was isolated case

Peach Bottom Atomic Power Station has not been cited even though a plant worker falsified records on two occasions, according to the U.S. Nuclear Regulatory Commission.

An NRC investigation substantiated that a low-level worker deliberately falsified fire-protection-surveillance records without the knowledge of plant management, according to an NRC document dated April 30.

Plant officials ran an investigation into the matter and fired the worker, the document states.

Exelon Nuclear checked the records of other operators to determine if anyone else was involved in the falsification of the records. The commission determined that the violation resulted from the isolated actions of one worker.

-Report by Sean Adkins of the York Dispatch

- May 15, 2007- NRC finds partial-flow line under full-line use

Peach Bottom Atomic Power Station credited individuals with performing the functions of a "senior operator" who were not actually senior operators (SOs). Technical specifications and federal code require a certain number of hours and functions to be done by SOs. NRC inspectors discovered that another classification of worker was performing tasks which SOs were to be doing, as required under the plant's license.

The finding was classified as Green, with "very low safety significance." Owner Exelon was not cited, according to the NRC report of an inspection that ended March 31, 2007.

The report also noted that a partial-flow flush line (part of a high pressure coolant injection (HPCI)/reactor core cooling line), was being used for full-flow testing. The use, for which the line was not designed, resulted in cracked piping to the torus, which had to be replaced, according to the NRC report.

The finding was called "more than minor" and the report said the issue had been complex to evaluate. The matter was given Green categorization as "the probability of a large early release remained low."

Inspectors also found that procedures for effluent monitoring were inadequately established and maintained. Procedures were not adequate to detect "non-representative sampling of the 'B' train of the main stack particulate effluents sampling system."

The finding potentially affects public health and safety, but was considered of very low safety significance because it did not involve radioactive material. The NRC report also noted that personnel were not trained properly in the procedures.

None of the violations were cited, according to the NRC.

-Report by Marlene Lang

- June 26, 2007 -NRC finds 2 violations, untimely corrections, makes no citations

An NRC inspection completed on April 21, 2006 reported that in March 2006 Peach Bottom operators failed to ensure that test procedures for the high pressure coolant injection (HPCI) and the reactor core isolation cooling (RCIC) pump had acceptance criteria incorporating limits from design documents. Failing to stay within the limits for which the pump was designed could degrade the pump to a lower limit could interfere with proper flow and discharge pressure. The subsequent inspection, completed May 18, 2007, found that the March 2006 problem was not corrected.

The NRC inspectors reported that Peach Bottom owner Exelon had not revised the procedure "and had continued to conduct the surveillance test 13 times since the issue was discovered by the NRC."

An Exelon evaluation found the pumps currently met the design basis requirements and were operable, according to the report. "Exelon failed to take prompt corrective actions to address a safety issue in a timely manner," commensurate with safety significance and complexity," the report stated.

The matter did not result in citation because it did not represent a loss of system safety function.

A second violation also did not receive citation. Peach Bottom failed to correct a condition deemed "adverse to quality" for 22 months. The condition was associated with pressure boundary leakage, the NRC report explained. In July 2005 the NRC noted the plant had not promptly evaluated a steam leak on a high pressure coolant injection valve. The NRC report said Exelon "did not take corrective actions to address a safety issue in a timely manner."

- July 30, 2007 -Inspection notes failures to follow procedures

The NRC followed up on a fire and other problems at the Peach Bottom Atomic Power Station in a three-month inspection that ended June 30.

No citations were made for three incidents, two of which involved violations of NRC requirements, according to the Nuclear Regulatory Commission report.

An incorrect size matchup on a breaker caused a fire at the '4T4' 480 volt load center, NRC inspectors explained in a report that followed up on the "Unusual Event."

The February 2007 fire was a result of human error, according to the report, which explained that "an incorrect frame size breaker was installed into a cubicle for which it was not sized. This mismatch caused an electrical fault that led to a fire and a plant transient that upset plant stability." Operators responded to the fire and "equipment losses" by cutting reactor power to half its normal rate.

NRC inspectors determined the "root cause" of the fire to be "that standards, policies, and administrative controls were not used." Maintenance technicians did not strictly follow instructions to verify the frame size during the overhaul of a spare breaker.

The finding was labeled Green and "of very low safety significance" because it did not increase the likelihood of a plant shutdown or the likelihood that mitigation equipment functions would not be available.

The report also noted that a missed procedure step in a surveillance test resulted in an unplanned overloading of an emergency diesel generator on March 15, 2007. This also was due to human error, according to the NRC report, which explained that workers did not follow procedure when the overload happened.

Other emergency generators remained operable. The generator that was overloading was out of service for less than the specified outage time allowed, of seven days. The finding was labeled Green and Exelon was not cited.

In a third Green finding, the NRC said operators failed to follow procedures while manipulating a diesel-driven fire pump cooling water valve on May 23, 2007. The improper manipulation led to misalignment of the fire pump cooling water that subsequently damaged the entire engine during operations without cooling water, the report explained. The fire pump was rendered inoperable by the damage to the engine.

The report said operators were not provided complete and accurate instruction for cleaning the cooling water strainer, which contributed to the situation. The finding was considered of very low safety significance.

Exelon was not cited.

-Report by Marlene Lang

- Aug. 31, 2007 -Performance review by NRC give good marks

The Nuclear Regulatory Commission announced the completion of its performance review of the Peach Bottom Atomic Power Station for the first half of 2007. The report said the plant operated in such a way as not to require any additional NRC oversight beyond the regularly scheduled inspections. Those inspections were outlined in the letter to Exelon president Christopher Crane.

-Report by Marlene Lang

- August 2007- File closed on allegation

NRC's Region I office which oversees Peach Bottom closed the file on the allegations made in a letter by a Wackenhut Corp. supervisor that security officers were working too long and taking naps on duty, saying the accusation was unsubstantiated.

-Report by Marlene Lang

September 2007 -News station WCBS in New York provided the NRC Region I office with a videotape that depicted inattentive security officers on duty at the Peach Bottom Atomic Power Station. "The videotape was broadcast on national television and resulted in considerable congressional and public concern," an NRC memo noted in Aug. 2008.

- Baltimore Examiner summary of Peach Bottom sleeping guards incidents

March: John Jasinski sends the Nuclear Regulatory Commission a letter alleging guards are sleeping throughout the nuclear plant in York County, Pa. The NRC refers the concern to plant owner Exelon and security provider Wackenhut.

Sept. 10, 2007- WCBS in New York informs the NRC that it has a videotape of guards asleep or nodding off in a “ready room” near the nuclear reactor.

Sept. 21, 2007- An NRC inspection confirms only the 10 guards caught on tape were sleeping — only one of four shifts is implicated.

Nov. 1, 2007- Exelon terminates its contract with Wackenhut and takes over the plant’s security. Whistle-blower Kerry Beal, on leave during the investigation, is not among the Wackenhut guards rehired by Exelon.

Nov. 5, 2007- NRC inspectors follow up at Peach Bottom to ensure Exelon is correcting the problem.

December 2007-2008: NRC pledges to monitor Peach Bottom.

Baltimore Examiner, December 12, 2007

- Nov. 28, 2007 -Security issues prompt more inspections for Peach Bottom

Between March and August of 2007, Kerry Beal videotaped 10 of his fellow Wackenhut Corp. officers at the Peach Bottom plant napping in a secure location of the plant while on the job.

Beal reportedly tried to report the incidents within his chain of command on duty, but then turned the tape over to WCBS news in New York.

The incident prompted Exelon to fire Wackenhut from serving at the Peach Bottom plant. Exelon will conduct more inspections and is reviewing whether to continue contracts with Wackenhut for security at Exelon's other nine nuclear power plants.

An NRC investigation also found officers has slept on duty at least four times between February and August 2007. However, the NRC determined that the plant's security program was not significantly degraded as a resulted.

Increased NRC inspections will review the plant's transition to an in-house security force.

-Report by Garry Lenton of the Patriot News

- Feb. 5, 2008- Peach Bottom plant repairs safety valve

Peach Bottom Atomic Power Station operators shut down Unit 3 this morning to repair a safety valve.

The valve prevents steam lines to the electric turbine from becoming over-pressurized, said Bernadette Lauer, power station spokeswoman.

In a release, Lauer said the plant's operators are investigating the cause of the equipment malfunction. There was no risk to the public, she said.

Unit 2 continues to operate at full power. Units 2 and 3 are boiling water reactors, and Unit 2 is capable of generating approximately 1,138 net megawatts and Unit 3 is capable of generating approximately1,140 net megawatts.

-Report by York Daily Record/Sunday News

Feb. 8, 2008 -Peach Bottom Atomic Power Station's Unit 3 reactor came back online at 3:30 p.m. Thursday after workers had replaced a safety relief valve that had malfunctioned earlier this week.

Peach Bottom's Unit 2 reactor continued to operate at full power without interruption during the Unit 3 shutdown.

-Report by Sean Adkins of the York Dispatch

- Feb. 14, 2008- Inspection finds one violation

An integrated inspection by the NRC found one violation deemed of low safety significance at the Peach Bottom Atomic Power Station, according to a report by the Nuclear Regulatory Commission. Exelon was not cited for the "failure to include the reactor building equipment and floor drain plugs in the scope of the Maintenance Rule program." Because of this, the station "did not recognize that appropriate preventive maintenance was not being performed," the report stated.

Inspectors noted that the finding indicated a failure of problem identification and resolution, because the procedures did not contain lessons learned from a similar event in February 2007.

-Report by Marlene Lang

- March 3, 2008 -Annual Assessment calls for heightened oversight of guards, security

The NRC has called for "additional regulatory oversight" of Peach Bottom's performance, as a result of security officer inattentiveness revealed in the last quarter of 2007. The inspection covered all of 2007 and the plant was found to have performed satisfactorily in areas related to reactor and radiation safety.

However, enhanced oversight will include additional inspections in the areas of security force performance monitoring, corrective actions, safety conscious work environment (SCWE) and completion of commitments.

The Nuclear Regulatory Commission's report on the annual inspection told Exelon that "behaviors and interactions within the security organization did not encourage the free flow of information related to raising safety issues."

This presumably was a reference to media reports that the Wackenhut Corp. security officer who videotaped his fellow officers sleeping on the job, claimed he had tried to report the problem within the work environment and was met with no action, before he gave the recording to local media.

The plant receive a White rating for the violations.

-Report by Marlene Lang

Here is a brief recount of the events which led to the heightened oversight:

December 2007-2008: NRC pledges to monitor Peach Bottom.

Baltimore Examiner, December 12, 2007

- April 9, 2008- NRC announcing meeting with Exelon over safety issues

Officials of the Nuclear Regulatory Commission will meet with Exelon Generation Co. representatives to discuss the results of an NRC inspection that focused on "safety conscious work environment" (SCWE). The inspection and the meeting are in response to incidents related to Wackenhut Corp. security offiicers who were found sleeping on the job and the related issue of why incidents were not reported before a worker took a videotape to the media. Wackenhut has provided security guards on a contract basis to several of Exelon's plants, but since the incident, Peach Bottom and others have turned to in-house security.

The NRC requires that license holders, like Exelon, "maintain an environment in which safety issues are promptly identified and effectively resolved and employees feel free to raise safety concerns," according to an NRC announcement of the April 15 meeting.

In another NRC press release the same day, the agency proposed a $130,000 civil penalty against a nuclear power plant in Florida, 30 miles south of Miami, after a 2006 investigation found Wackenhut-employed security officers there sleeping on duty over a period of two years. The release said that on April 6, 2006, a security officer was seen by an NRC inspector sleeping while on duty at a post in a vital area of the reactor.

-Report by Marlene Lang

- May 6, 2008- Fire bridgade 'deficient'

An integrated inspection of the Peach Bottom Atomic Power Station by the NRC ended March 31, 2008 and resulted in one "more than minor" finding that was not cited.

According to the report, numerous fire brigade deficiencies were not discussed at a post-drill critique or documented in a fire drill record, resulting in fire brigade deficiencies. Among the undocumented deficiencies: the brigade opened a hot door to a fire area with no protective equipment on; the supervisor gave orders to sway, rather than shut down, lubricating oil pumps during the fire, failing to take the most conservative action as required. This failure went unrecognized by other team members and evaluators. Also, the fire brigade was not aware of the status of the sprinkler system, to ensure that it was actuated, and the team failed to set the ventilation system to remove smoke from the room, until prompted by the drill instructor.

The crew with observed "deficiencies" was one of five on site, and the only one with problems.

The violation was not cited.

-Report by Marlene Lang

- May 9, 2008- Emergency exercises assessed, need improvement: FEMA

A regional administrator for FEMA informed Maryland's Director of Emergency Management that the Federal Emergency Management Agency (FEMA) and the Department of Homeland Security held radiological emergency preparedness exercised at Peach Bottom Atomic Power Station on April 22, 2008 and that four deficiencies occurred during the exercises.

One deficiency was that Harford County, Md., emergency operations were not coordinated with other jurisdictions and were not preceded by siren activation.

There were similar coordination problems with Cecil County, Md., where problems arose related to communication with media during an emergency. Maryland municipalities participate in the exercises because of their proximity to the Peach Bottom plant in southern York County, Pa.

-Report by Marlene Lang

- May 21, 2008- Inspectors: Required battery test was not being performed

In an NRC Component Design Bases inspection completed April 11, 2008, one violation was identified at the Peach Bottom Atomic Power Station.

According to the NRC's report, Exelon, owner of Peach Bottom, did not verify that certain battery connection resistances were within the limits of technical specifications. The report stated that Exelon had exempted the inter-tier connections (those between cells using cables vise steel bars) from the testing requirement. When Exelon did perform the exempted test, it was discovered that one of four cables on a Unit 2 battery was about the specified limit.

An evaluation of the violation showed the degraded connection would not have prevented the battery from fulfilling its safety function, the report stated.

Because safety function was not lost, the finding was given a Green rating and was not cited.

-Report by Marlene Lang

- May 27, 2008- Work environment study complete

After heightened oversight and additional inspections following incidents of sleeping guard, the NRC reported on its inspection of 'safety conscious work environment,' (SCWE). Exelon was to resolve work environment issues related to inattentive security guard issue identified in Sept. 2007.

According to the NRC report on the special inspection, 150 employees of the Peach Bottom plant participated in discussions on work environment issues. Inspectors determined that the SCWE survey was conducted in a manner that encouraged candid and honest responses and that survey results compared "favorably with industry norms." Exelon determined that there were some negative perceptions of the Employee Concerns Program among workers, regard confidentiality and effectiveness.

There were also perceptions of inconsistent standards and direction during refueling outages, and Exelon was to address this and other "perceptions" about adverse reaction for raising issues. During focus group meetings, inspectors could not find any instances where retaliation had happened as a result of someone raising safety issues, the report stated.

The report noted that Exelon had already begun the transition to an in-house security force.

The report said Exelon's self-assesment "resulted in a reasonabley complete understanding of the SCWE" at Peach Bottom.

-Report by Marlene Lang

- June 5, 2008- Radioactivity dose assessment not adequate, NRC says

Exelon violated federal code by not providing a means to continually assess the impact of the release of radioactive materials, in its 'dose assessment' program. According the a Nuclear Regulatory Commission report on an evaluation of an April 23 emergency preparedness exercise.

The assessment procedures and programs at the Peach Bottom plant limited assessment to only those conditions in which "the fuel clad barrier was lost or potentially lost," with instruction to operators telling them, in fact, not to take dose assessment protective action in cases where there was no loss or potential loss of the fuel clad. the report explained.

The report stated, The (NRC) inspectors observed during the April 23, 2008 exercise that before the fuel clad barrier had been declared potentially lost, a plant release was in progress while radiation readings in the Unit 2 drywell exceeded 600 rad/hour."

Inspectors noted that otherwise, asssessments were being conducted as prescribed.

The finding was classified as Green and of very low safety significance and was not cited, the report stated.

-Report by Marlene Lang

June 25, 2008 -NRC inspectors found three violations of "very low safety significance" in a team inspection completed May 16 at Peach Bottom.

The findings were rated Green and Exelon was not cited. NRC documents specifying the nature of the violations were not available.

- July 15, 2008- NRC checks on progress in sleeping guard remedies

The Nuclear Regulatory Commission continued its follow-up response to inattentive security officers and issues related to "safety conscious work environment" (SCWE) with an inspection at the Peach Bottom plant. The June 6, 2008 visit was to determine Exelon's progress in meeting the commitments it made to address the issues.

The inspection looked into the transition from a contracted to an in-house security force, a review of Peach Bottom's evaluation of the "root cause" of the problem and its effectiveness and an inspection of activities related to work environment issues (SCWE).

The NRC reported that no findings of significance turned up in the inspection and all actions to which Peach Bottom committed were considered closed, with two exceptions. Exelon would have to perform safety conscious work environment surveys at its other plants, and those survey results would have to be discussed.

It also remains for Exelon to submit written confirmation that all items have been completed.

-Report by Marlene Lang

- Aug. 12, 2008 -Material found in sprinkler system valve

An integrated inspection of Peach Bottom Atomic Power Station completed on June 30, 2008 by the NRC noted only on finding of "very low safety significance."

The Green level finding was made by maintenance personnel who discovered foreign material inside a supply valve to an automatic 13KV switchgear sprinkler system. The system is important to the plant's fire protection program. The material was removed.

Exelon was not cited.

-Report by Marlene Lang

Aug. 22, 2008- Regional NRC office under review for response to sleeping guards

Office of Inspector General find Region I assessment 'inconsistent'

The NRC Office of the Inspector General reviewed whether its Region I office responded adequately in handling the letter it received in March 2007 alleging security officers were sleeping on the job at Peach Bottom, and concluded the Region I office was inconsistent in its response.

(For background, see Chronology entries beginning March 20, 2007.)

According to a memo from the Inspector General to the Region I office of the NRC, the regional staff received the letter on March 27 and held a board meeting to evaluate it on March 29 and again on April 11, 2007. Prior to the two board meetings, an NRC engineer had been assigned to check out the relevant history of allegations at Peach Bottom. The engineer returned an e-mail report on March 28, stating there had been three previous allegations in 2005 related to Peach Bottom security; one about overtime and fatigue, one concerning retaliation against security officers and one allegation of security officers sleeping in the towers.

None of the allegations were substantiated, the engineer reported, also noting that there were some inconsistencies in the stories of the sleeping officers because it would be impossible to observe anyone sleeping inside the towers from outside.

The review also discussed an interview the Inspector General's office made of the Wackenhut security manager who made the original report of the inattentiveness. That manager said there was a fear of retaliation among guards, and said he had reported that fear to Exelon and Wackenhut. He also said he told Exelon that conditions in the "ready room" at the Peach Bottom plant were "not conducive to remaining alert." The ready room is an area where officers not on patrol may relax, but are ready to respond as needed.

The manager said he had suggested in a March 2007 letter approaches for catching the sleeping guards.

The Wackenhut manager claimed he had forwarded his concerns to the NRC on behalf of the security officers because they afraid of retaliation if they raised concerns, according to the memo.

NRC's Region I office referred the March 2007 concerns to Exelon in a letter on April 30, 2007. Three concerns were emphasized: 1) guard sleeping on duty, 2) guards fearing retaliation if they reported safety concerns, and 3) that Exelon was aware of the officers sleeping on duty and was not taking action.

Exelon responded in a letter on May 30, 2007, saying the concerns were not substantiated, based on several points. 1) Exelon had measures in place to reduce potential for inattentiveness, such as random radio checks, requirements for officers to walk around every 15 minutes, random observations of officers in the tower post, and supervisor visits twice per 12-hour shift. 2) Interviews did not confirm the allegations, 3) reviews of corrective actions reports did not show reluctance to report safety problems, and 4) officer work hour averages were lower than NRC limits.

The NRC Inspector General office noted that the NRC's May 30, 2007 letter did not contain any documents to support its evaluation of the safety concerns. The memo also explained that the two Exelon investigators who reviewed the March 2007 concerns concluded that the allegations were unsubstantiated. The Inspector General also noted that those Exelon investigators said at the time that they would have liked to have had more information from the Region I office about the concerns. But Region I said, in the past, Exelon had asked for more information when needed.

In May 2007, the Region I Division of Reactor Projects recommended the allegation file be closed, the memo said. The Region I Division of Reactor Safety delved into Exelon's response in a bit more detail, looking at how the random checks were implemented, how often, how many officer were checked and how checks were documented. That director concluded, also in May, that Exelon's response to the safety concerns was reasonable and sufficient in both depth and scope.

However, an engineer for the Division of Reactor Projects noted that Exelon might have interviewed a larger number of personnel, and said that he was unaware, at the time he made his review of Exelon's response to the concerns, that no security officers were interviewed from the team with the allegedly inattentive officers.

NRC's Region I Division of Reactor Safety pointed out that Exelon never explained exactly what was meant by "random observations," whether that meant post checks or visual observation and noted that observation of the Bullet Resistant Enclosure (BRE) tower guards was "not feasible." Others on the Region I staff agreed it would be hard to "sneak up" on BRE guard to check on inattentiveness.

The NRC's Office of the Inspector General found that the NRC's Region I office was "inconsistent" in its assessment of the safety significance of the two allegations, made within six months of each other, expressing similar concerns about inattentive security officers at the Peach Bottom Atomic Power Station. The inconsistencies were in relation to allegations that officers feared retaliation if they reported safety concerns, and the allegation that Exelon was aware that officers were inattentive on duty but did not take action to address the matter.

The Inspector General's report noted that the Region I staff did not question the information they were given by Exelon and did not probe or attempt to verify it.

The NRC memo said that Region I staff could have contacted the former Wackenhut security manager to obtain more specifics, could have provided Exelon with more detailed information, could have provided the information to the NRC's resident inspectors at Peach Bottom for increased monitoring of guard activities, and could have assigned Region I security inspectors to look into the March 2007 concerns during a baseline inspection that took place from April 30 to May 4, 2007.

-Report by Marlene Lang

Aug. 28, 2008- Inspection procedures complete regarding inattentive guards

NRC: Matter closed

The Nuclear Regulatory Commission completed its inspection and review of Peach Bottom's "inattentive security guard events" and concluded that "the licensee (Exelon) has adequately addressed the commitments/actions described in (Confirmatory Action Letter) 1-07-005; the NRC has reasonable assurance that the Peach Bottom facility will continue to be operated safely; and adequate corrective actions have been taken to prevent reoccurrence of the underlying issues that led to the inattentive security officer events."

A letter to Exelon from the NRC said that the company would be expected to fulfill its commitment to conduct "safety conscious work environment" (SCWE) surveys of security organizations at all it nuclear reactor sites it identify any actions that need to be taken, and to inform the NRC by Oct. 31, 2008 of survey completion so that a meeting can be scheduled to discuss the results.

Additionally, the NRC gave Exelon a "White" level safety finding related to the incidents and for having "an ineffective behavior observation program."

-Report by Marlene Lang

- Aug. 29, 2008- Supplemental inspection finds nothing 'significant'

Inspectors conclude management of guards was 'inadequate'

An NRC inspection, completed July 25, 2008, examined Exelon's response at Peach Bottom to a previous "White" level finding related to inattentive security officers. The report on the supplemental inspection stated no findings of significance were identified.

The report also stated that Exelon's comprehensive evaluation of the security officer inattentiveness issue determined three root causes. They were: 1) Inadequate Exelon management oversight and leadership of Wackenhut Nuclear Security management to ensure appropriate security force perfomance. 2) Wackenhut Nuclear Security failed to provide adequate oversight of security force performance, and 3) an adverse culture of inattentiveness and non-compliance with the behavior observation program existed within the Peach Bottom Atomic Power Station security organization.

The report stated Exelon had addressed the issue acceptably, but the matter would be considered in assessing plant performance in future assessments, through the third quarter of 2008.

-Report by Marlene Lang

Sept. 10, 2008- WCBS in New York informs the NRC that it has a videotape of guards asleep or nodding off in a “ready room” near the nuclear reactor.

Sept. 21, 2008- An NRC inspection confirms only the 10 guards caught on tape were sleeping — only one of four shifts is implicated.

- Oct. 10, 2008 -Water leak in containment area not analyzed

NRC inspectors found Peach Bottom Atomic Power Station Unit 1 reactor had failed to perform periodic radiological analysis of water in the containment vessel, as required by federal code.

An inspection conducted in July and August 2008 found that water that had accumulated in the containment vessel on the 87-foot, 9-inch elevation under a removable floor plate in a hallway was not analyzed. The water "intruded" into the Unit 1 containment vessel and the radioactive waste building, the report stated. The water accumulated was less than the code specification limit of 500 gallons. According to the report, the water had been there since "at least January 2005."

The finding was considered a Level IV violation, but was not cited, as Exelon "initiated a plan to restore compliance."

Inspectors also found that Peach Bottom had failed to properly keep records related to decommissioning, not maintaining or referencing the location of all required records "important to the safe and effective decommissioning of the facility." The site file contained a list of "spills and released from 1976 to 2004" but it did not contain other required records and their locations, as code demands.

Owner Exelon was not cited for the Level IV violation.

-Report by Marlene Lang

Nov. 1, 2008- Exelon terminates its contract with Wackenhut and takes over the plant’s security. Whistle-blower Kerry Beal, on leave during the investigation, is not among the Wackenhut guards rehired by Exelon.

Nov. 5, 2008- NRC inspectors follow up at Peach Bottom to ensure Exelon is correcting the problem.

A Sept. 30, 2008 inspection of the Peach Bottom Atomic Power Station, Units 2 and 3 by the Nuclear Regulatory Commission found three violations by owner Exelon Generation Company LLC, though no citation were made.

In a self-revealing non-cited violation, a failure to follow procedure was revealed after an emergency service water leak (ESW) was discovered on the E-1 emergency diesel generator (EDG), according to the NRC's report, dated Nov. 13, 2008. The report said the leak "resulted in safety-related equipment being adversely affected."

The NRC determined the finding was of "very low safety significance," or Green level, because it did not represent an actual loss of system safety function.

Also, a transformer fire and petroleum spill were not properly reported to the NRC, according to the NRC report. A Level IV Severity event, NRC inspectors noted the NRC was not notified by the Peach Bottom Power Station of the reportable event on July 23 and 24, 2008. Inspectors found a planned press release and notification of other government agencies concerning the transformer fire and petroleum spill. The NRC report state "the failure to make a required report could adversely impact the NRC's ability to carry out its regulatory mission," and that the event was related to public health and safety as it contributed to the loss of the plant's three offsite power sources. The event was also noted as an environmental protection issue because "it involved the spill of more than minor quantity of oil the required reporting to the state of Pennsylvania."

Because the NRC had been "informally notified," the NRC determined the finding was a non-citation violation.

NRC inspectors also found the Peach Bottom plant did not conduct a sufficient quality assurance program, adequate to identify incorrect gamma spectroscopy analyses of a principal gamma emitting radionuclide used to scale hard-to-detect radionuclides for purposes of waste classification in accordance with 1- CFR  61.55. The report noted, "The failure to conduct a sufficiently robust quality assurance program ... is a performance deficiency that was reasonably within the licensee's ability to foresee and correct." The NRC called the finding "more than minor" because it affect the plant's "cornerstone objective" by failing to identify incorrectly anylyzed samples used to classify radioactive waste for land disposal.

The finding was considered of "low safety significance" because no radiation limits were exceeded, there was no breach of packaging and no certificate of compliance finding, no low-level burial ground non-conformance, and no failure to make notifications or provide emergency notification.

- Report by Marlene Lang

November 13, 2008- NRC inspects Peach Bottom plant, finds three violations, makes no citations

- Dec. 10, 2008- Hunters trespass on power plant property

Several hunters were found to be trespassing on company property in the vicinity of the north substation of the Peach Bottom Atomic Power Station.

The incident was classified as an Event of Potential Public Interest (EPPI) by officials, who issued a report for Units 2 and 3 around 1 p.m. on Dec. 10.

The state Department of Environmental Protection Bureau of Radiation Protection was notified along with Military and Veteran Affairs, the Public Utility Commission, state police, officials of Chester, York and Lancaster counties and PEMA's central office.

-Report by Marlene Lang

May 12, 2009- NRC inspection finds plant departed from code in analyzing spent fuel pools

NRC inspectors who completed a quarterly inspection of the Peach Bottom Atomic Power Station on March 31, 2009 found three violations at the plant.

Two were rated “Green” findings but a third was considered a Severity Level IV violation, but none were cited, according to the NRC report of the inspection.

In one case, NRC inspectors reported that inadequate work instructions resulted in a momentary shorting of a terminal lead during maintenance, causing an inadvertent one-hour shutdown of reactor Unit 3. A containment isolation valve signaled the shutdown.

The report explained, “Work instructions allowed technicians to lift and manipulate energized leads on a safety-related pressure switch, without providing any guidance as to the risk and consequences that inadvertent grounding of those leads could cause.”

The report also stated that the failure “could reasonably be viewed as a precursor to a major event.” The valves in question “failed closed,” the report stated, and “did not represent an actual open pathway in the physical integrity of reactor containment.”

The failure to “provide appropriate risk insights” to workers was a human performance and work control issue, according to the inspectors’ report.

This finding was rated Green and was not cited.

In another “Green” inspection finding, a partial shutdown of the Unit 3 reactor occurred on Jan. 26, 2009 when the ‘A’ Wide-Range Neutron Monitoring (WRNM) became inoperable due to “inadequate procedural guidance regarding adjustments to the mean square voltage offset during the outage.”

The same NRC report described workers’ failure to make a “smooth transition” when shutting down the Unit 3 reactor to replace a main transformer, triggering a partial shutdown or “half-scram,” in industry terms.

The full explanation of the incident explained that the neutron monitor read a certain noise as mean square voltage (MSV) fluctuation within the reactor core. To compensate, the MSV was adjusted to a value of 8E9, though the MSV offset cannot be set higher than 3E8. According to the report, a system manager had specifically said this, but personnel performing the work did not “address the comments,” and this mis-adjustment caused the failed “smooth transition” and a sudden shift in the WRNM, which in turn generated the shutdown signal.

An NRC analysis of the incident concluded that the “deficiency,” or cause of the incident was the use of only two, instead of the required three operable WRNMs, on the Reactor Protection System (RPS) trip, when transferring to “Mode 2.”

The Severity Level IV code violation was noted because the Peach Bottom plant had used a spent fuel pool criticality analysis methodology that was not previously approved by the NRC, departing from the code-prescribed method and failing to obtain NRC approval or a license amendment to do so.

The methodology relates to degraded Boroflex in the high density spent fuel storage racks. Peach Bottom was using a formula to calculate density that differed from the federal code’s formula, mixing existing and new methodologies within the system.

The finding could affect the functionality of the fuel barrier (cladding), the report said, but stated the condition was of very low safety significance.

Peach Bottom agreed to correct the problem by coming up with an evaluation method adequate for testing safety of the spent fuel pool storage racks in accordance with federal code.

2010

Sept. 22, 2010 – Plant officials notify NRC at 5:53 p.m. that a number of emergency sirens lost power during a thunderstorm that passed through York County and Harford County, Md. Plant said 21 emergency sirens lost power in York County and eight sirens lost power in Harford County. Because more than 25 percent of the sirens were unavailable, the following agencies were contacted: Pennsylvania and Maryland Emergency Management; Harford and Cecil counties in Maryland; and Lancaster, Chester and York counties in Pennsylvania.

Sept. 30, 2010- On Sept. 30, 2010, the NRC issued a report on an audit conducted on units 2 and 3 during Dec. 16-17, 2009. An audit is conducted every three years to determine whether licensee programs are consistent with industry guidance.

In the audit, the NRC said Peach Bottom implemented NRC commitments on a timely basis for licensing activities and has implemented an adequate program for managing NRC commitment changes. The NRC also found that there were some discrepancies regarding the implementation of some commitments.

The audit found that there was a non-implemented commitment relating to “fuel moving and core loading with secondary containment inoperable (plant shutdown)” at units 2 and 3. The NRC said the licensee did not implement the commitment it received in September 2008, and “did not process a commitment change to evaluate and document this decision.” The NRC said this discrepancy was entered into the licensee’s correction action program.

The audit also found issues relating to the use of Delta Mururoa BLU respiratory suits. . “The licensee indicated that the associated commitments had not been implemented since the suits have not been used” at Peach Bottom, the NRC report said. “However, the NRC staff noted that there was no indication in the commitment tracking system documenting that the site did not have to comply with the commitment until the suits were used.”

The audit found that Peach Bottom had not developed a lesson plan for training, and had partially implemented commitments with the manufacturer for reporting any defects of the suits, and the proper procedures in case the suits begin to lose air, condensation appears on the visor, or the wearer feels unusual warmth.

The audit also found there were complications regarding the use of two tracking systems and inadequacies in the assignment of commitments at the corporate level. ”Corporate and site personnel have access to both systems, but a manual interface is required to coordinate the two systems,” the NRC report said. “The NRC staff identified issues regarding the tracking of fleet wide commitments” at Peach Bottom, the report said. “One such commitment was to revise the placement of dosimetry in response to the use of new

weighting factors for the determination of the deep-dose equivalent for external exposures.’

According to the NRC report, the licensee “found that the commitment had not been routed to the plant site correctly, and therefore, did not appear in the licensee’s search.“ The discrepancy was entered into the plant’s corrective action program, the NRC said.

Oct. 22, 2010 – A helium leak was discovered in a cask that stores spent nuclear

fuel. The cask was located within the Unit 3 containment building at the Peach

Bottom Atomic Power Station.

According to the NRC, a preliminary review showed “that a leak exists at the

weld plug that provides sealing of the drilled interseal passageway associated

with the drain port penetration of the cask lid.” It added, “This leak effectively

provides a bypass of the main lid outer confinement seal.

Plant officials said they were working with a vendor to repair the leak, and no

radiation had been released.

Nov. 10, 2010- The NRC issued its findings from an integrated inspection

conducted at Units 2 and 3 at the Peach Bottom plant for the third quarter

ending Sept. 30.

Based on the inspection, the NRC said it identified one non-cited violation of very low safety significance. It was entered into the plant’s corrective action program.

The finding involved the failure to adhere to technical specifications to make

sure that adequate voltage was available to all safety-related components

required to respond to a loss-of-coolant accident.

“The licensee must demonstrate that the existing degraded voltage trip setpoints… are adequate to protect and provide the required minimum voltage to all safety-related

equipment,” the NRC said. “Since load tap chargers (which plant operator Exelon used in its calculations) are not safety-related and are subject to operational limitations and credible single failures, they cannot be relied on to establish degraded voltage relay setpoints and time delay input for design basis calculations.”

The NRC said it informed Exelon that the voltage levels used in its calculations were not correct, and “to show safety-related equipment would be operable

during design basis events, the technical specifications degraded grid relay

setpoints must be used.” It added that Exelon performed electrical calculations

using the most limiting voltage levels allowed by the specs, and “determined

that multiple components would not have adequate voltage.”

On another matter in the report, the NRC inspectors focused on a Nov. 12, 2009,

non-cited violation when Exelon implemented a temporary configuration

change without a review that would have likely required a license amendment

before its implementation. In response to this incident, the NRC said, “The

inspectors concluded that Exelon has identified and taken appropriate actions to

resolve the issues …The inspectors reviewed the procedure revision and

determined that the new changes were appropriate to address the program gaps

that existed in the old revision.”

The NRC report also noted there was an unresolved item dealing with potential procedural inadequacies during fuel handling incidents in the reactor core and spent fuel pool from Sept. 18 to Sept. 24, 2010.

“The events appear to be examples where inadequate procedures contributed to fuel handling issues,” the NRC said. “This issue will remain unresolved pending completion of Peach Bottom’s investigation and cause evaluation processes under

the corrective action program.”

May 13, 2011 – The NRC said there would be no significant environmental impact with the transfer of low-level radioactive waste from the Limerick Generating Station in southeastern Pennsylvania to a storage facility at the Peach Bottom plant.

Peach Bottom officials initially requested a license amendment to allow the transfer of the waste on Jan. 6, 2010. The waste does not include any transfer of spent nuclear fuel from Limerick.

- Exelon operates both nuclear power plants.

The Limerick plant does not have the capacity to store all of the low-level radioactive waste it generates. The NRC noted that the Barnwell disposal facility in South Carolina is

no longer available for Limerick, but Peach Bottom has the ability to store a large amount of low-level waste on an interim basis.

In its environmental analysis, the NRC noted that there would be two or three shipments a year from Limerick to Peach Bottom. “The distance between the plant sites is less than the distance that was previously traveled to the Barnwell disposal facility in South Carolina,” the NRC noted.

“The staff concludes that the radiological impacts associated with the transportation, handling and storage of low-level radioactive waste at Peach Bottom will not result in a significant impact to plant workers and members of the public,” the NRC said.

“The proposed action will not significantly increase the probability or consequences of accidents. No changes are being made in the types of effluents that may be released offsite. There is no significant increase in the amount of any effluent released offsite. There is no significant increase in occupational or public radiation exposure. Therefore, there are no significant radiological environmental impacts associated with the proposed action.”

Sept. 18, 2011 – The York Daily Record reported that an injured Peach Bottom worker was transported to York Hospital while wearing a contaminated work glove. The glove was covered by a bag and handled by a radiation protection technician, but was not

removed due to the worker’s injuries, the newspaper reported. Once the ambulance arrived at the hospital, the glove was removed, tested and transported back to the plant.

No contamination was passed to surrounding areas, Peach Bottom spokesman David  Tillman told the newspaper.

The incident occurred while the worker was fixing a valve at Unit 3 of the plant, which was in shutdown mode for maintenance and refueling. The paper said a valve the worker was examining closed on the fingertips of his left hand.

Nov. 10, 2011 – The NRC issued its inspection report for Units 2 and 3 completed for the third quarter ending Sept. 30, 2011.

No findings of significance were identified. However, a licensee-identified violation was determined to be of very low safety significance and was treated as a non-cited violation.

Nov. 17, 2011 – An NRC inspector conducted a routine safety inspection of Unit 1 at the Peach Bottom Atomic Power Station on Oct. 26-27, 2011. Unit 1 is a gas-pooled demonstration power reactor that operated from February 1966 through October 1974, and has been permanently shut down and in safe storage since then.

Based on the inspection, no issues of safety significance were identified, the NRC said in a letter.

Dec. 15, 2011 – The NRC issued a report on the inoperability associated with an offsite power circuit at Units 2 and 3. This situation was confirmed on Nov. 16, 20101, and is a violation of technical specifications

The NRC report said modifications performed in the mid-1990s failed to upgrade the reliability of offsite sources, essentially minimizing redundancies.

Technical specifications require that there be two qualified circuits between offsite transmission networks and Units 2 and 3, the NRC said. “With one offsite circuit inoperable, the inoperable circuit must be returned to an operable status within seven days or the unit must be brought to a hot shutdown condition within 12 hours,” the NRC report said. There were two occasions in 2010 (March and May) when this requirement was not met, the NRC said. There was another period in 2010 as well, but the violation did not exceed seven days.

- “There were no actual safety consequences associated with this event,” the NRC said.

Feb. 10, 2012 – The NRC issued its report of the quarterly inspection of Units 2 and 3 for the period ending Dec. 31, 2012. The report said there were four findings, two identified by the licensee Exelon that were of very low safety significance.

One NRC finding involved a failure to establish and implement an adequate quality assurance program regarding effluent and environmental monitoring of Units 2 and 3. “The finding is more than minor because it is associated with the public radiation safety cornerstone attribute of programs and processes,” the NRC report said. “The licensee reassessed the dose to members of the public from routine releases and determined that projected doses did not, nor were likely to, exceed applicable limits,” the NRC added.

The violation related to the finding “is currently under review by the NRC,” the report said.

NRC inspectors said it identified six examples where the effluent and environmental quality assurance program was ineffective. Among the examples: Exelon did not conduct an evaluation of its 2010 land use census results that show a need for additional monitoring stations; Exelon did not conduct an assessment of its long-term meteorological data to compare the 2010 results against long-term averages; Exelon’s failure to evaluate its first, second and third quarter 2011 inter-laboratory samples to determine if sample analyses met applicable quality assurance requirements; and a failure to conduct its onsite biennial evaluation for liquid tritium analysis during its second quarter 2011 sample activity.

“The failure to establish, implement and maintain such a quality assurance program were reasonably within Exelon’s ability to foresee and should have been prevented,” the NRC said.

The NRC added, “There was no indication of a spill or release of radioactive material on the licensee’s site or to the offsite environment that would impact public dose assessments and there was no substantial failure to implement the radioactive effluent release program. There was no effluent monitor calibration issue and the licensee had data by which to assess dose to a member of the public. Exelon plans to provide updated effluent release and dose reports, as necessary, to reflect revised analyses.”

Another finding involved Exelon’s failure to correct a safety related matter of a motor-operated valve. “Specifically, corrective actions to prevent recurrence of motor-operated valve program testing failures due to degraded stem lubrication in 2009 were not performed in a timely manner to prevent the inoperability of a safety related” valve, the NRC said. It noted that a valve did not develop sufficient thrust during diagnostic testing on Sept. 22, 2011, and “would not have been able to perform its safety function to close during the most limiting design condition.”

The report observed that Peach Bottom officials determined that degraded motor-operated valve stem lubrication resulted in four safety-related program failures in March and April of 2009. It was found that the lubricant should be changed, noting that the vendor for the old lubricant canceled production in 2001. At the time, Peach Bottom began a transition to another lubricant for its motor-operated valves, a process that was to be completed by the end of 2014.

By the end of 2011, 128 of the 182 motor-operated valves had been transitioned to a different grease, the NRC report said. Based on a review, 14 motor-operated valves had their conversion dates moved up, and Peach Bottom said it decided to expedite its correction program to complete the transition process by the end of 2013, not 2014.

The NRC report also listed two licensee-identified violations that were of very low safety significance. One involved a failure to perform maintenance that affected an emergency diesel generator. “Specifically, Peach Bottom determined that a damaged lubrication oil drain line should have been identified and replaced during planned maintenance activities prior to the occurrence of leakage,” the report said.

Peach Bottom also found that a particular pump was in inoperable during a period of time from April 27, 2010, to Oct. 2, 2011. Officials determined that a leaking relief valve body could have become detached from a residual heat removal suction piping, resulting in the pump’s inoperability. Peach Bottom “determined the cause of the delay in identifying the inoperable condition was due to inadequate technical rigor when evaluating the operability of the relief valve on April 27, 2010,” the NRC said. The leaking valve was replaced on Oct. 2, 2011.

The NRC also commented on an issue regarding the start time for a 15-minute classification period of a fire. (See previous reports dated Sept. 12, 2011, with both Peach Bottom and Three Mile Island.) The NRC had said the Peach Bottom policy decreased the effectiveness of the plant’s emergency plan. The NRC said Exelon entered the matter into its corrective action program and implemented a revision. “The inspectors determined that Exelon’s response and corrective actions were reasonable and appropriate to address the non-cited violation and finding and their underlying  performance deficiency, “ the NRC said. “The NRC considers the issue to be closed.”

The NRC also observed that Peach Bottom was appropriately identifying and entering issues into its corrective action program. However, the inspectors did note some ominous trends, including issues of industrial safety and equipment reliability.

It noted that there were three Occupational Safety and Health Administration recordable injuries in September 2011, and there were 45 first aid events during the September/October 2011 Unit 3 refueling outage

The report also noted that Peach Bottom submitted five event reports related to degraded or failed equipment from June 1 to Dec. 31, 2011. “The inspectors verified that all of the equipment issues identified … have been entered’ the plant’s corrective action program, the NRC said.

NRC inspectors also evaluated the performance of an emergency drill on Dec. 5, 2011. No problems were identified.

July 23, 2012 – The NRC issued a letter to Peach Bottom officials informing them of some security inspection issues in January 2011.

Specifically, the NRC said its Office of Investigations determined that a security lead supervisor and a security officer “willfully falsified security post inspection documentation.” The incidents occurred on Jan 16 and Jan. 25 in 2011, the NRC said.

On these two dates, the NRC said, the lead supervisor did not physically access security posts to conduct inspections that are designed to make sure the security officer is attentive to duties and is free from any condition that would detract from workplace performance. On those two days, the NRC said, the lead supervisor contacted the security officer by phone, and then forged the security officer’s signature on a post inspection form with the security officer’s consent. “Additionally,” the NRC said, “the security officer forged the lead supervisor’s signature on the post activity log with an entry indicating the inspection had been conducted.”

The NRC said the violation was of very low safety significance because, “although the (lead supervisor) did not access the post locations on those occasions to monitor the environmental conditions and to monitor the assigned security officer for attentiveness and signs of fatigue, other (plant) security supervisors inspected those posts both before and after the (lead supervisor) failed to do so. Additionally, when the lead supervisor contacted the security officer by telephone, the security officer answered the telephone.”

The NRC said that corrective actions were take by the plant, including disciplinary action against the lead supervisor and the security officer, and training with security department personnel on the proper procedures for signing logs.

The OI completed its investigation on April 11, 2012.

September 12, 2012

About 50 workers at Peach Bottom nuclear plant exposed to

low levels of radiation

Peach Bottom Atomic Power Station in Peach Bottom

Township. (FILE)

York, PA -

Roughly 50 workers at Peach Bottom Atomic Power Station were exposed to low levels of radiation early Tuesday after a discharge of contaminated steam. At 1 a.m. that morning, workers were loosening a two-inch vent on top of the Unit 2 reactor vessel head when a "puff" of radioactive steam escaped from a flange, said Neil Sheehan, a spokesman for the U.S. Nuclear Regulatory Commission. Radiation monitoring alarms sounded as workers, dressed in bright yellow radiation-protection suits, hurried to close the vent. In total, the length of the release lasted about 2 minutes.

The reactor is offline for a planned refueling outage. About 2,000 contracted or outage workers at the plant will spend the next several weeks completing maintenance work and replacing nearly one-third of the reactor's fuel.

Initially, 51 of the 138 workers stationed in the area of the Unit 2 reactor vessel early Tuesday didn't clear the plant's radiation monitors, meaning that they still registered a higher dose of contamination, Sheehan said. After a change of clothes and a shower, seven of the 51 workers no longer triggered the monitors.

Of the remaining workers, 27 had been exposed to more than 10 millirems of radiation and 17 registered a dose of less than 10 millirems. A millirem is a measure of radiation exposure. One worker came back with a dose of 173 millirems- the highest level of exposure tied to the radioactive

steam, Sheehan said.

"For that employee, follow-up monitoring shows that contamination levels have fallen off and, today, are

almost at the level of being undetectable," said David Tillman, a Peach Bottom spokesman.

The occupational radiation exposure limit for nuclear industry workers is 5,000 millirems per year, Sheehan

said.

The average American citizen is exposed to 610 millirems each year from natural and manmade sources, he

said.

What happened?

On Tuesday morning, as workers disassembled the vent, a step in the process of refueling Unit 2, water

levels inside the reactor were higher than expected, Sheehan said.

Nov. 14, 2012 – The NRC issued its report on its inspection of Units 2 and 3 of the Peach Bottom Atomic Power Station for the third quarter ending Sept. 30.

In the report, the NRC identified one self-revealing finding of very low safety significance. In addition, the report listed one licensee-identified violation determined to be of very low safety significance.

The NRC finding involved the failure of the plant operator to avoid a situation during maintenance activities of the lower pressure coolant injection system at Unit 2.

The incident occurred on July 25, 2012, when electricians were performing an electrical cable pull “for the multiple spurious operations project into the Unit 2 energized low pressure coolant injection swing bus motor control cabinet.” During the pull, lubrication contacted one of the electrician’s gloved hands and caused the hand to suddenly slide up the cable and contact the edge of an adjacent interposing closing relay, the report said. The contact actuated the relay, the report added, resulting in an over current alarm in the control room

The NRC said the potential over-thrust event “called into question the qualification and operability of the valve.”

The report added, “The inspectors noted that the workers performed a two-minute-drill to assess the hazards and safety concerns in the work area, but did not consider the possibility of lubrication contacting their work gloves and causing their hands to slip during the cable pull. The inspectors also noted that the operational risk of the cable pull was not communicated to the workers.”

The report also mentions a Sept. 11, 2012, review of radiological issues due to the release of steam during the opening of the reactor vent line flange at Unit 2. “A total of 47 individuals received internal uptakes and were whole body counted,” the report said. “There was no radioactive release from the rector building due to this event.”

The licensee identified violation involved the failure to promptly correct defective welds in the E-3 emergency diesel generator lube oil piping that were identified in 1998. A leak was identified in the piping during surveillance testing on Sept. 3, 2012.  Corrective action was taken.